## Abstract
BOQ FOR REHABILITATION AND UPGRADATION OF NH-4 (NEW NH-69) FROM NALAGAMPALLI (EXISTING K.M. 171.590/DESIGN CH:172+000) TO AP/KARNATAKA BORDER (EXISTING KM.216.912/DESIGN CH:219+687)
S. No | Work Description | UOM | PR BOQ Qty | Rate | Amount | Reason
1 | Earthing:
1.1 | Supply and installation of 20 dia 1 Meter Long MS rod for Street Lighting Pole Earthing | Nos. | 1050 |  |  | For Damaged Poles 35 Nos and 10 Nos all Booth at Toll Plaza
1.2 | Supply and Installation of 8 SWG GI wire for Street Lighting pole body and scope shall inclusive of making end terminations | Mtr | 26500 |  |  | Above Said 1.1 (Each will have 6.5 Mtrs)
1.3 | Supply and Installation, Testing and commissioning of 25 X3 mm Hot galvanized GI strip for Feeder Pillar Earthing | Mtr | 150 |  |  | (Each will have 2 Mtrs) for Below said 1.4 reason
1.4 | Supply and Installation, Testing and commissioning of 40 dia 2 meter long Chemical Earthing | Nos. | 100 |  |  | For High Mast 4 Nos and 3 Nos for Office Container Cabins
2 | Street Lighting Feeder Panels
2.1 | SITC of IP65 Outdoor Lighting Feeder Panel suitable for 415V, 3 Phase, 4 Wire, 50Hz AC supply, complete with 100A, 4 Pole MCCB incomer (36kA breaking capacity), SPD(Type 1+2, 3P+N, 40 kA), R-Y-B LED phase indication lamps, 3 Nos. 6A SP control MCBs, 1 No. Astronomical Timer, 1 No. Single Phasing Preventer with Over Voltage and Under Voltage protection, Auto/Manual selector switch with OFF position, 100A 4 Pole Contactor contactor, 63/100A Aluminium Electrical Grade Busbars (3P+N) with supports and acrylic shrouding, 12 Nos. SP outgoing MCBs of 32A( 10kA breaking) ratings, connectors, neutral and earth bars, complete internal power and control wiring with copper cables, ferrules, lugs, DIN rails, PVC wiring channels,danger plate, name plate of the panel and all associated accessories. The panel shall be housed in an IP65 outdoor type double-door enclosure fabricated from 1.6mm thick GI sheet with 3mm thick gland plate, complete with canopy, door gasket, locking arrangement, bottom cable entry provision, earth studs and mounted on a 1000mm high MS stand. The panel shall be supplied complete in all respects including assembly, inspection, testing and commissioning as per technical specifications. | Nos | 35
2.2 | SITC of IP65 Outdoor Lighting Feeder Panel suitable for 415V, 3 Phase, 4 Wire, 50Hz AC supply, complete with 63A, 4 Pole MCCB incomer (36kA breaking capacity),SPD(Type 1+2, 3P+N, 40 kA), R-Y-B LED phase indication lamps, 3 Nos. 6A SP control MCBs, 1 No. Astronomical Timer, 1 No. Single Phasing Preventer with Over Voltage and Under Voltage protection, Auto/Manual selector switch with OFF position, 63A 4 Pole contactor, 63A Aluminium Electrical Grade Busbars (3P+N) with supports and acrylic shrouding, 12 Nos. SP outgoing MCBs of 20A( 10kA breaking) ratings, connectors, neutral and earth bars, complete internal power and control wiring with copper cables, ferrules, lugs, DIN rails, PVC wiring channels,danger plate, name plate of the panel and all associated accessories. The panel shall be housed in an IP65 outdoor type double-door enclosure fabricated from 1.6mm thick GI sheet with 3mm thick gland plate, complete with canopy, door gasket, locking arrangement, bottom cable entry provision, earth studs and mounted on a 1000mm high MS stand. The panel shall be supplied complete in all respects including assembly, inspection, testing and commissioning as per technical specifications. | Nos | 5
2.3 | SITC of IP65 Outdoor Lighting Feeder Panel suitable for 415V, 3 Phase, 4 Wire, 50Hz AC supply, complete with 40A, 4 Pole MCCB incomer (36kA breaking capacity), SPD(Type 1+2, 3P+N, 40 kA), R-Y-B LED phase indication lamps, 3 Nos. 6A SP control MCBs, 1 No. Astronomical Timer, 1 No. Single Phasing Preventer with Over Voltage and Under Voltage protection, Auto/Manual selector switch with OFF position, 25A 3 Pole AC-3 power contactor, 63A Aluminium Electrical Grade Busbars (3P+N) with supports and acrylic shrouding, 12 Nos. SP outgoing MCBs of 16A( 10kA breaking) ratings, connectors, neutral and earth bars, complete internal power and control wiring with copper cables, ferrules, lugs, DIN rails, PVC wiring channels,danger plate, name plate of the panel and all associated accessories. The panel shall be housed in an IP65 outdoor type double-door enclosure fabricated from 1.6mm thick GI sheet with 3mm thick gland plate, complete with canopy, door gasket, locking arrangement, bottom cable entry provision, earth studs and mounted on a 1000mm high MS stand. The panel shall be supplied complete in all respects including assembly, inspection, testing and commissioning as per technical specifications. | Nos | 5
3 | Poles & Fixtures
3.1 | Supply, Transportation, Erection cabling and commissioning of New 10 mtr hot-dip galvanized octagonal pole with j Bolts, Which includes unloading, shifting to the installation location lifting using suitable crane/skylift positioning alignment tightening of foundation bolts with nuts and washers earthing connection to the pole and making the pole ready for cable termination and commissioning. Civil foundation works excavation concreting and grouting are excluded from the scope. The work shall be completed in all respects as per approved drawings and the instructions of the Engineer-in-Charge. | Nos | 40 |  |  | Required for Accidental damage Rectifcation compliance works
3.2 | SITC of high-quality integrated LED Street Light with a minimum system lumen of 38250 lm and system wattage not exceeding 225W with a nominal system efficacy of 170 lumen/watt. The LED used shall have CCT of 5700K, SDCM ≤ 5 and CRI≥70. The housing should be made of non-corrosive Single Piece pressure die-cast aluminum, to withstand extreme environments. The spigot shall be part of “Single Piece Pressure Die-cast housing” & shall not be bolted to the luminaire housing to ensure robust design. The name of the brand should be embossed/engraved & should not be mentioned using sticker/screen printing. It should have corrosion resistant powder coating to pass NSS of 500 Hrs. The luminaire LED shall have declared Lifetime of 75K hours@L70. The product should be designed for continuous operation (10-12 Hrs. per day). The Ingress protection should be minimum IP66 & impact resistance shall be IK10. The minimum luminaire dimensions shall be L: 630mm, W: 255MM, H: 135MM & nominal weight shall be 3.8KG (±5%). Control gear compartments shall be Top maintainable without accessing/opening the optical compartment. The Luminaire should have a minimum 10 KV/5KA SPD duly bolted in the Luminaire. The SPD should be able to sustain a minimum 15 hits of 5KA rating i.e. Total of 45 hits across all the three modes as per IEEE 62.41.2. The luminaire should be of Class B Serviceability. The LED used in the luminaire shall be SMD type only & shall be from either Lumileds, Osram, Nichia, Cree & APT Electronics make or equivalent. The Driver should be asphalt potted & should be a BIS approved driver. The driver shall have operating voltage of 120V to 270V, PF≥0.95 (@ full load), THD≤10% (@ full load). The driver should be capable of withstand voltage stress of 440V for 8 Hrs., should have an auto shutdown @ 325V(±15V) and have an auto recovery feature. The driver shall comply to EMI/EMC standard EN 55015, IEC61547 & IEC 61000-3-2. The luminaire brand name shall be embossed/engraved on the luminaire/end plate & not screen printed or put using sticker. The luminaire driver & it’s SPD shall be of the same make/manufacturer as that of LED luminaires. Luminaire manufacturer must have In-house NABL accredited lab to conduct LM79, Type test as per IS10322, "FAT" before dispatch as per IS 10322 & IK Test. The the successful bidder must submit the NABL accreditation certificate for Luminaire manufacturer before supply of material. The LED Luminaire & it's driver both should be BIS registered. Successful bidder shall submit the following reports before supply of material for approvals LM79 issued by NABL accredited lab, LM80 issued by LED manufacturer, Type Test Certificate for luminaire as issued by NABL accredited lab, BIS certificate for LED Luminaire & Driver. Similar to above Specs in Signify (Philips/Ecolink)BRP505 LED382 CW R5C PSU S2 SPD or equivalent | Nos | 900 |  |  | Additional Stock purposes and Required for Accidental damage Rectifcation compliance works
3.3 | SITC of high-quality integrated LED Street Light with a minimum system lumen of 29750 lm and system wattage not exceeding 175W with a nominal system efficacy of 170 lumen/watt. The LED used shall have CCT of 5700K, SDCM ≤ 5 and CRI≥70. The housing should be made of non-corrosive Single Piece pressure die-cast aluminum, to withstand extreme environments. The spigot shall be part of “Single Piece Pressure Die-cast housing” & shall not be bolted to the luminaire housing to ensure robust design. The name of the brand should be embossed/engraved & should not be mentioned using sticker/screen printing. It should have corrosion resistant powder coating to pass NSS of 500 Hrs. The luminaire LED shall have declared Lifetime of 75K hours@L70. The product should be designed for continuous operation (10-12 Hrs. per day). The Ingress protection should be minimum IP66 & impact resistance shall be IK10. The minimum luminaire dimensions shall be L: 630mm, W: 255MM, H: 135MM & nominal weight shall be 3.8KG (±5%). Control gear compartments shall be Top maintainable without accessing/opening the optical compartment. The Luminaire should have a minimum 10 KV/5KA SPD duly bolted in the Luminaire. The SPD should be able to sustain a minimum 15 hits of 5KA rating i.e. Total of 45 hits across all the three modes as per IEEE 62.41.2. The luminaire should be of Class B Serviceability. The LED used in the luminaire shall be SMD type only & shall be from either Lumileds, Osram, Nichia, Cree & APT Electronics make or equivalent. The Driver should be asphalt potted & should be a BIS approved driver. The driver shall have operating voltage of 120V to 270V, PF≥0.95 (@ full load), THD≤10% (@ full load). The driver should be capable of withstand voltage stress of 440V for 8 Hrs., should have an auto shutdown @ 325V(±15V) and have an auto recovery feature. The driver shall comply to EMI/EMC standard EN 55015, IEC61547 & IEC 61000-3-2. The luminaire brand name shall be embossed/engraved on the luminaire/end plate & not screen printed or put using sticker. The luminaire driver & it’s SPD shall be of the same make/manufacturer as that of LED luminaires. Luminaire manufacturer must have In-house NABL accredited lab to conduct LM79, Type test as per IS10322, "FAT" before dispatch as per IS 10322 & IK Test. The the successful bidder must submit the NABL accreditation certificate for Luminaire manufacturer before supply of material. The LED Luminaire & it's driver both should be BIS registered. Successful bidder shall submit the following reports before supply of material for approvals LM79 issued by NABL accredited lab, LM80 issued by LED manufacturer, Type Test Certificate for luminaire as issued by NABL accredited lab, BIS certificate for LED Luminaire & Driver. Similar to above Specs in Signify (Philips) BRP505 LED297 CW R5C PSU S2 SPD or equivalent | Nos | 930 |  |  | Additional Stock purposes and Required for Accidental damage Rectifcation compliance works
3.4 | SITC of high-quality integrated LED Street Light with a minimum system lumen of 25500 lm and system wattage not exceeding 150W with a nominal system efficacy of 170 lumen/watt. The LED used shall have CCT of 5700K, SDCM ≤ 5 and CRI≥70. The housing should be made of non-corrosive Single Piece pressure die-cast aluminum, to withstand extreme environments. The spigot shall be part of “Single Piece Pressure Die-cast housing” & shall not be bolted to the luminaire housing to ensure robust design. The name of the brand should be embossed/engraved & should not be mentioned using sticker/screen printing. It should have corrosion resistant powder coating to pass NSS of 500 Hrs. The luminaire LED shall have declared Lifetime of 75K hours@L70. The product should be designed for continuous operation (10-12 Hrs. per day). The Ingress protection should be minimum IP66 & impact resistance shall be IK10. The minimum luminaire dimensions shall be L: 630mm, W: 255MM, H: 135MM & nominal weight shall be 3.8KG (±5%). Control gear compartments shall be Top maintainable without accessing/opening the optical compartment. The Luminaire should have a minimum 10 KV/5KA SPD duly bolted in the Luminaire. The SPD should be able to sustain a minimum 15 hits of 5KA rating i.e. Total of 45 hits across all the three modes as per IEEE 62.41.2. The luminaire should be of Class B Serviceability. The LED used in the luminaire shall be SMD type only & shall be from either Lumileds, Osram, Nichia, Cree & APT Electronics make or equivalent. The Driver should be asphalt potted & should be a BIS approved driver. The driver shall have operating voltage of 120V to 270V, PF≥0.95 (@ full load), THD≤10% (@ full load). The driver should be capable of withstand voltage stress of 440V for 8 Hrs., should have an auto shutdown @ 325V(±15V) and have an auto recovery feature. The driver shall comply to EMI/EMC standard EN 55015, IEC61547 & IEC 61000-3-2. The luminaire brand name shall be embossed/engraved on the luminaire/end plate & not screen printed or put using sticker. The luminaire driver & it’s SPD shall be of the same make/manufacturer as that of LED luminaires. Luminaire manufacturer must have In-house NABL accredited lab to conduct LM79, Type test as per IS10322, "FAT" before dispatch as per IS 10322 & IK Test. The the successful bidder must submit the NABL accreditation certificate for Luminaire manufacturer before supply of material. The LED Luminaire & it's driver both should be BIS registered. Successful bidder shall submit the following reports before supply of material for approvals LM79 issued by NABL accredited lab, LM80 issued by LED manufacturer, Type Test Certificate for luminaire as issued by NABL accredited lab, BIS certificate for LED Luminaire & Driver. Similar to above Specs in Signify (Philips) BRP505 LED255 CW R5C PSU S2 SPD or equivalent | Nos | 960 |  |  | Additional Stock purposes and Required for Accidental damage Rectifcation compliance works
3.5 | SITC of high-quality integrated LED Street Light with a minimum system lumen of 34000 lm and system wattage not exceeding 200W with a nominal system efficacy of 170 lumen/watt. The LED used shall have CCT of 5700K, SDCM ≤ 5 and CRI≥70. The housing should be made of non-corrosive Single Piece pressure die-cast aluminum, to withstand extreme environments. The spigot shall be part of “Single Piece Pressure Die-cast housing” & shall not be bolted to the luminaire housing to ensure robust design. The name of the brand should be embossed/engraved & should not be mentioned using sticker/screen printing. It should have corrosion resistant powder coating to pass NSS of 500 Hrs. The luminaire LED shall have declared Lifetime of 75K hours@L70. The product should be designed for continuous operation (10-12 Hrs. per day). The Ingress protection should be minimum IP66 & impact resistance shall be IK10. The minimum luminaire dimensions shall be L: 630mm, W: 255MM, H: 135MM & nominal weight shall be 3.8KG (±5%). Control gear compartments shall be Top maintainable without accessing/opening the optical compartment. The Luminaire should have a minimum 10 KV/5KA SPD duly bolted in the Luminaire. The SPD should be able to sustain a minimum 15 hits of 5KA rating i.e. Total of 45 hits across all the three modes as per IEEE 62.41.2. The luminaire should be of Class B Serviceability. The LED used in the luminaire shall be SMD type only & shall be from either Lumileds, Osram, Nichia, Cree & APT Electronics make or equivalent. The Driver should be asphalt potted & should be a BIS approved driver. The driver shall have operating voltage of 120V to 270V, PF≥0.95 (@ full load), THD≤10% (@ full load). The driver should be capable of withstand voltage stress of 440V for 8 Hrs., should have an auto shutdown @ 325V(±15V) and have an auto recovery feature. The driver shall comply to EMI/EMC standard EN 55015, IEC61547 & IEC 61000-3-2. The luminaire brand name shall be embossed/engraved on the luminaire/end plate & not screen printed or put using sticker. The luminaire driver & it’s SPD shall be of the same make/manufacturer as that of LED luminaires. Luminaire manufacturer must have In-house NABL accredited lab to conduct LM79, Type test as per IS10322, "FAT" before dispatch as per IS 10322 & IK Test. The the successful bidder must submit the NABL accreditation certificate for Luminaire manufacturer before supply of material. The LED Luminaire & it's driver both should be BIS registered. Successful bidder shall submit the following reports before supply of material for approvals LM79 issued by NABL accredited lab, LM80 issued by LED manufacturer, Type Test Certificate for luminaire as issued by NABL accredited lab, BIS certificate for LED Luminaire & Driver. Similar to above Specs in Signify (Philips) BRP505 LED340 CW R5C PSU S2 or equivalent | Nos | 125 |  |  | Additional Stock purposes and Required for Accidental damage Rectifcation compliance works
3.6 | SITC of LED flood 50W having housing made of pressure die cast aluminium. The system wattage shall be 50W & the luminaire shall deliver minimum system lumens of 5000lumens. The system efficacy of the luminaire shall be ≥100lm/w. The LEDs used in the luminaire shall be from either Lumileds, Osram, Nichia, APT Electronics and CREE make, shall have CCT of 5700°K, CR≥70, SDCM≤5. The luminaire shall have IP rating of IP65 & IK rating of IK07. The luminaire shall have toughened glass. The LED driver shall have operating voltage range of 140V to 270V, PF≥0.95 @ full load, THD≤ 10% @ full load, In-built surge protection of 4KV Luminaire manufacturer must have In-house NABL accredited lab to conduct LM79, Type test as per IS10322. The LED Luminaire & it's driver both should be BIS registered. Successful bidder shall submit the following reports before supply of material for approvals LM79 issued by NABL accredited lab, LM80 issued by LED manufacturer, BIS certificate for LED Luminaire & Driver. Similar to SIGNIFY (PHILIPS) BVP173 LED55 CW 50W FG GR PSU or equivalent | Nos | 140 |  |  | Rounded off
4 | Pole Foundations and Rectifiaction Works
4.1 | Design construction casting curing and installation of reinforced cement concrete (RCC) foundation for street lighting poles suitable for the specified pole height and wind load as per IS 875 including excavation PCC bed reinforcement steel foundation J bolts templates grouting and all associated accessories. The work shall include backfilling compaction disposal of surplus earth curing of concrete alignment and levelling of foundation and making good the surrounding surface to its original condition | Nos | 40 |  |  | Required for Accidental damage Rectifcation compliance works
4.2 | Rectification of luminaire arm angle from the existing 5°/10° tilt angle to 0° tilt angle as per approved lighting design. The work includes loosening, adjusting, and realigning the arm brackets and luminaires to achieve a uniform 0° tilt angle, tightening all fasteners, and ensuring proper alignment and illumination distribution. The work shall be completed in all respects as per the approved drawings, lighting design requirements, and the instructions of the Engineer-in-Charge. | Nos | 300
4.3 | Adaptor Rectifiaction Work: Carry out thorough cleaning of the surface using a wire brush to remove rust, dirt, and loose particles. Apply a two-coat painting system with a total dry film thickness (DFT) of 120 microns, consisting of:One coat of Zinc Phosphate Primer, and One coat of Glossy Finish Silver Colour Paint as the final finishing coat. | Nos | 686
4.4 | Electrical Streete light Pole Door Rectification: Supply of access door for octagonal pole fabricated from suitable gauge MS sheet complete with hinges locking arrangement gasket nuts bolts and all necessary accessories. The door shall be suitable for installation on octagonal poles and conform to the pole manufacturer s specifications | Nos | 1690
5 | LTXPLE UG Cables , DWC Duct pipes
5.1 | Supply and laying of 4 C X 6 Sq. MM. XLPE insulated armoured cable of 1.1 KV grade as per IS 7098,(includeing end Termination of the cables with Lugs for all the cables and DC glands etc.) | Mtrs | 8500 |  |  | Rounded off
5.2 | Supply and laying of 4 C X 10 Sq. MM. XLPE insulated armoured cable of 1.1 KV grade as per IS 7098,(includeing end Termination of the cables with Lugs for all the cables and DC glands etc.) | Mtrs | 9500 |  |  | Rounded off
5.3 | Supply and laying of 4 C X 16 Sq. MM. XLPE insulated armoured cable of 1.1 KV grade as per IS 7098,(includeing end Termination of the cables with Lugs for all the cables and DC glands etc.) | Mtrs | 11700 |  |  | Rounded off
5.4 | Supply and laying of 4 C X 25 Sq. MM. XLPE insulated armoured cable of 1.1 KV grade as per IS 7098,(includeing end Termination of the cables with Lugs for all the cables and DC glands etc.) | Mtrs | 15200 |  |  | Rounded off
5.5 | Supply and laying of 4 C X 35 Sq. MM. XLPE insulated armoured cable of 1.1 KV grade as per IS 7098,(includeing end Termination of the cables with Lugs for all the cables and DC glands etc.) | Mtrs | 9600 |  |  | Rounded off
5.6 | Supply and laying of 4 C X 50 Sq. MM. XLPE insulated armoured cable of 1.1 KV grade as per IS 7098,(includeing end Termination of the cables with Lugs for all the cables and DC glands etc.) | Mtrs | 2200 |  |  | Rounded off
5.7 | Supply and Laying of 3 C X 1.50 Sq. mm. Cu flexible wire cable of 1.1 KV grade as per IS 7098, .(include end Termination of the 3 C X 1.50 Sq. mm. Cu. Flexible cable with Lugs for all the cables including material ) | Mtr | 26000 |  |  | Rounded off
5.8 | Supply and Laying of 40 mm DWC Duct Pipe conforming to IS 14930 (Part II), including excavation of trenches to the required depth, laying of the duct with necessary couplers and accessories, cable routing from feeder pillar to poles and pole-to-pole locations, backfilling with excavated soil, proper compaction, and restoration of the surface to its original condition. The work shall be carried out in accordance with relevant IS standards for cable laying and trenching. The scope includes all materials, labour, tools, transportation, testing, and completion of the work in all respects. | Mtr | 19400 |  |  | Rounded off
5.9 | Supply and laying of 40 mm HDPE DWC (Double Wall Corrugated) duct pipe conforming to IS 14930 (Part II), including breaking of existing PCC where required, excavation of trench to the specified depth, laying of DWC duct with proper alignment, backfilling with excavated soil in layers and compaction, and restoration of the top surface with PCC concrete to match the existing finish. The work shall be completed in all respects as per relevant IS standards and the Engineer-in-Charge's instructions. | Mtr | 15000 |  |  | Rounded off
5.1 | Supply and laying of 40 mm HDPE DWC (Double Wall Corrugated) duct pipe conforming to IS 14930 (Part II), including fixing the duct along the concrete cross barrier with suitable clamps at 1.0 m intervals for pole-to-pole cable routing. The scope includes all necessary accessories, fittings, supports, and fastening materials required for complete installation. The work shall be executed in a neat and workmanlike manner, ensuring proper alignment and protection of the duct, and completed in all respects in accordance with the relevant IS standards and the instructions of the Engineer-in-Charge. | Mtrs | 24000 |  |  | Rounded off
5.11 | Pole cable termination shall include the supply and installation of suitable Hylam sheets, 1/2 Nos. 6A MCBs(for Each light Fixure 1MCB), 63A RYB connectors, and cable lugs of appropriate sizes as per the cable specification. All terminations shall be carried out properly with neat workmanship, ensuring safe, secure, and reliable electrical connections. | No | 1700 |  |  | Rounded off
5.12 | Horizontal Directional Drilling (HDD) for cable laying, including drilling, supply and installation of 63 mm HDPE Pipe, PE-100 grade, PN 10, conforming to IS 4984, suitable for underground heavy-duty road crossing (pulling of cable, restoration of disturbed surfaces, and all associated works complete as per relevant IS standards and as per NHAI guidelines) and the Engineer-in-Charge's instructions. HDD shall be carried out at all road crossings and locations where open trench excavation is not permitted | RMT | 2600
5.13 | Road cutting for cable laying, including excavation, supply and installation of GI pipe for cable protection, laying of cable through the GI pipe, backfilling, and restoration of the road surface to its original condition(fill with Concrete). The work shall be carried out in accordance with relevant IS standards and as directed by the Engineer-in-Charge | Mtrs | 0 |  |  | Omitted and will use the Qty 5.9
5.14 | New Service Connection: Scope includes - New Service Connection from application to Meter Connection Which Includes New Transformer, 11 KV Service Line with PCC poles and new meter connection and All applicable deposits charges and Liaisoning will come under vendor scope. The Minimum requirement of Transformer will be 16 KVA 11kV/230V Single Phase Oil Immersed Distribution Transformer complete with all standard fittings accessories earthing and outdoor mounting arrangement for highway lighting load applications and all incoming and outgoing UG Cables to be provided to nearby feeder pillar locations.. | Nos | 5
6 | Additional BOQ as per Site Requirement
6.1 | Supply of New GI Single Arm 1.5 Mtrs and installation on the existing 10 Mtrs GI Octagonal pole including unloading shifting to the installation location lifting using suitable crane/skylift positioning alignment tightening of foundation bolts with nuts and washers earthing connection to the pole and making the arm ready for Light Fixture installation. | Nos | 20 |  |  | Accidental Damage rectification and stock purposes
6.2 | Supply of New GI Double Arm 1.5 Mtrs and installation on the existing 10 Mtrs GI Octagonal pole including unloading shifting to the installation location lifting using suitable crane/skylift positioning alignment tightening of foundation bolts with nuts and washers earthing connection to the pole and making the arm ready for Light Fixture installation. | Nos | 20 |  |  | Accidental Damage rectification and stock purposes
6.3 | Supply and Fixing of LED flood 70W having housing made of pressure die cast aluminium. The system wattage shall be 70W & the luminaire shall deliver minimum system lumens of 9800lumens. The system efficacy of the luminaire shall be ≥140lm/w. The LEDs used in the luminaire shall be from either Lumileds Osram Nichia APT Electronics and CREE make shall have CCT of 5700°K CR≥70 SDCM≤5. The luminaire shall have IP rating of IP65 & IK rating of IK07. The luminaire shall have toughened glass. The LED driver shall have operating voltage range of 140V to 270V PF≥0.95 @ full load THD≤ 10% @ full load In-built surge protection of 4KV Luminaire manufacturer must have In-house NABL accredited lab to conduct LM79 Type test as per IS10322. The LED Luminaire & it s driver both should be BIS registered. Successful bidder shall submit the following reports before supply of material for approvals LM79 issued by NABL accredited lab LM80 issued by LED manufacturer BIS certificate for LED Luminaire & Driver. Similar to SIGNIFY (PHILIPS) BVP173 LED55 CW 50W FG GR PSU or equivalent | Nos | 35 |  |  | For Toll Plaza Canopy, Each Booth will have 3 Nos*10 and 5 nos for bike lane
|  |  |  | Total Amount==>> | 0

## Earthing
BOQ Breakup of Earthing and its associates accessoires
S.No | Description | Total Nos of poles / Qty | Considered Nos of Poles / Qty | Each will have | Total Qty | Comments
1.1 | 20 dia 1 Meter Long MS rod for Street Lighting Pole Earthing | 1690 | 1004 | 1 | 1004 | Except VUP locations - DI Arm Poles (686 Nos)
1.2 | 8 SWG GI wire for Street Lighting pole | 1690 | 1004 | 1.5 | 26202
|  |  | 686 | 36 |  | For Clamping
1.3 | 25 X3 mm Hot galvanized GI strip for Feeder Pillar Earthing | 45 | 45 | 3 | 135 | For Feeder Pillers each 3 mtrs
1.4 | 40 dia 2 meter long Chemical Earthing | 45 | 45 | 1 | 93 | For Feeder Pillers Each 1 no's
|  | 12 | 24 | 2 |  | For DI Arms, consider 4 Nos. per stretch, comprising 2 Nos. on the Left-Hand Side (LHS) and 2 Nos. on the Right-Hand Side (RHS).
4.3 | Adaptor Rectifiaction Work: | 1690 | 686 | 1 | 686

## Feede Pillar List
BOQ Breakup of Feeder Pillars
Sr. No | Chainages |  | Side | Feeder Panel | Rating Type
| From | To
2 | 172+430 | 172+520 | LHS | 1 | 100A
4 | 172+620 | 173+960 | RHS | 1 | 100A
8 | 174+871 | 175+830 | LHS | 1 | 100A
| 174+871 | 175+830 | RHS | 1 | 100A
11 | 177+210 | 178+670 | LHS | 1 | 100A
| 177+210 | 178+670 | RHS | 1 | 63A
12 | 178+670 | 180+410 | LHS | 2 | 100A
| 178+670 | 180+410 | RHS | 2 | 100A
18 | 182+070 | 182+900 | LHS | 1 | 100A
| 182+070 | 182+900 | RHS | 1 | 63A
19 | 182+900 | 184+045 | LHS | 1 | 100A
19 | 182+900 | 184+045 | RHS | 1 | 63A
22 | 184+540 BUS BAY |  | BHS | 1 | 40A
24 | 191+150 BUS BAY |  | BHS | 1 | 40A
27 | 192+061 | 192+500 | LHS | 1 | 100A
27 | 192+061 | 192+500 | LHS | 1 | 63A
28 | 192+120 | 193+500 | RHS | 1 | 100A
31 | 194+260 | 195+700 | BHS | 4 | 100A
34 | 196+270 | 197+640 | BHS | 2 | 100A
38 | 199+800 | 200+520 | LHS | 1 | 100A
39 | 199+800 | 200+520 | RHS | 1 | 100A
41 | 200+895 | 201+100 | LHS | 1 | 100A
44 | 201+760 | 202+400 | BHS | 2 | 100A
49 | 206+100 | 206+350 | RHS | 1 | 100A
52 | 207+630 BUS BAY |  | RHS | 1 | 63A
57 | 209+680 | 210+700 | BHS | 2 | 100A
61 | 211+420 | 213+160 | LHS | 3 | 100A
62 | 213+160 | 214+430 | LHS | 2 | 100A
64 | 214+800 BUS BAY |  | LHS | 1 | 40A
68 | 215+940 | 216+820 | LHS | 2 | 100A
70 | 217+565 BUS BAY |  | LHS | 1 | 40A
72 | 218+450 | 218+800 | LHS | 1 | 100A
74 | 219+180 BUS BAY |  | LHS | 1 | 40A
TOTAL |  |  |  | 45
| Rating | Qty
| 100A | 35
| 63A | 5
| 40A | 5

## LED Lights
Chainagewise BOQ - Ch 173+550 to 219+500
Sr. No | Chainages |  | Distance | TCS | Pole to Pole Distance | Pole Arragnement | 10 Mtrs Pole with 1.5 mtr O deg Double arms |  |  | 10 Mtrs Pole with 1.5 mtr O deg Single arms |  |  | 10 Mtrs Pole with 1.5 mtr O deg and 1.5 mtr O deg Differantial arms |  |  | Damaged Poles | Removal Poles proposal | Road Cutting | HDD | Fedder Panel | 226 Watt | 198Watt | 175 Watt | 151watt | Remark
| From | To |  |  |  |  | Median | LHS | RHS | Median | LHS | RHS | Median | LHS | RHS
1 | 172+550 BUSBAY |  |  | TCS 2 | 25 | RHS Side | [5 empty] | 6 | [5 empty] | 9 | [5 empty] | 6
2 | 172+430 | 172+520 |  | TCS 1B | 30 | Median | 4 | [11 empty] | 1 | 1 | 8
3 | 172+520 | 173+680 |  | TCS 6 |  | LHS Side |  | 8 |  |  | 16 |  |  | 34 |  | 2 | 11 |  |  |  | 42 | 8 | 8 | 42 | 5(VUP LHS)+2(LHS END)
4 | 172+620 | 173+960 |  | TCS 8 |  | RHS Side | [5 empty] | 53 |  |  |  | 8 | 8 | 9 |  | 1 |  | 53
5 | 173+770 | 173+860 |  | TCS 1B | 30 | Median | 4 | [11 empty] | 1 |  | 8
6 | 174+650 BUS BAY |  |  | TCS 1B |  | LHS Side/ RHS Side |  |  |  |  | 6 | 6 | [5 empty] | 16 | [5 empty] | 12
7 | 174+765 | 174+855 |  | TCS 9 |  | Median | 5 | [11 empty] | 1 |  | 10
8 | 174+871 | 175+830 |  | TCS 6 |  | LHS Side/ RHS Side |  | 8 | 8 |  | 8 | 8 |  | 23 | 23 |  | 8 |  |  | 2 | 62 |  | 16 | 62
9 | 175+870 | 175+930 |  | TCS 1B |  | Median | 3 | [11 empty] | 1 |  | 6
10 | 177+110 | 177+200 |  | TCS 1B |  | Median | 4 | [11 empty] | 1 |  | 8
11 | 177+210 | 178+670 |  | TCS 6 |  | LHS Side/ RHS Side |  | 23 | 10 |  | 9 |  |  | 23 | 23 | 2 |  | 10 |  | 2 | 79 |  | 9 | 79
12 | 178+670 | 180+410 |  | TCS 5 |  | LHS Side/RHS Side |  | 66 | 66 | [8 empty] | 40 |  | 4 |  |  | 264
13 | 178+480 BUSBAY |  |  | TCS 2 |  | RHS Side |  |  | 6 | [8 empty] | 9 | [5 empty] | 6
14 | 179+380 BUSBAY |  |  | TCS 2 |  | LHS Side |  | 6 | [8 empty] | 6 | 9 | [5 empty] | 6
15 | 179+810 BUSBAY |  |  | TCS 2 |  | RHS Side |  |  | 6 | [7 empty] | 6 | 9 | [5 empty] | 6
16 | 180+420 | 180+540 |  | TCS 1B |  | LHS Side/ RHS Side |  |  |  |  | 3 | 3 | [5 empty] | 18 |  |  |  |  | 6
17 | 181+950 | 182+070 |  |  |  | LHS Side/ RHS Side |  |  |  |  | 4 | 4 |  |  |  | 2 |  | 18 |  |  |  |  | 8
18 | 182+070 | 182+900 |  | TCS 6 |  | LHS Side/ RHS Side |  | 7 | 7 |  |  |  |  | 18 | 18 | 1 |  | 10 |  | 2 | 50 |  |  | 50
19 | 182+900 | 184+045 |  | TCS 5 |  | LHS Side/ RHS Side |  | 34 | 34 | [8 empty] | 20 |  | 2 |  |  | 136
20 | 183+250 BUSBAY |  |  | TCS 2 |  | LHS Side |  |  |  |  | 6 | [5 empty] | 6 | 10 | [5 empty] | 6
21 | 184+030 | 184+045 |  |  |  | LHS Side/ RHS Side |  |  |  |  | 3 | 3 | [5 empty] | 20 |  |  |  |  | 6
22 | 184+540 BUS BAY |  |  | TCS 2 |  | LHS Side |  |  |  |  | 6 | [7 empty] | 1 | 1 |  |  |  | 6
23 | 184+760 BUSBAY |  |  | TCS 2 |  | RHS Side | [5 empty] | 6 | [11 empty] | 6
24 | 191+150 BUS BAY |  |  | TCS 2 |  | LHS Side |  |  |  |  | 6 | [7 empty] | 6 | 1 |  |  |  | 6
25 | 191+500 BUSBAY |  |  | TCS 2 |  | RHS Side | [5 empty] | 6 | [11 empty] | 6
26 | 191+971 | 192+061 |  | TCS 1B |  | Median | 4 | [11 empty] | 1 |  | 8
27 | 192+061 | 192+500 |  | TCS 6 |  | LHS SIDE |  | 10 |  |  | 9 |  |  | 45 |  |  | 5 | 10 |  | 2 | 55 |  |  | 55
28 | 192+120 | 193+500 |  | TCS 8 |  | RHS Side | [5 empty] | 55 |  |  |  | 5 |  | 18 |  | 1 |  | 55
29 | 193+500 | 193+590 |  | TCS 1B |  | Median | 3 | [11 empty] | 1 |  | 6
30 | 194+150 | 194+230 |  | TCS11B |  | Median | 4 | [8 empty] | 1 |  |  | 1 |  | 8
31 | 194+260 | 195+700 |  | TCS 6 |  | LHS/RHS Side |  | 21 | 21 |  | 8 | 8 |  | 24 | 24 |  | 16 | 10 |  | 4 | 90 |  | 16 | 90
32 | 195+710 | 195+790 |  | TCS 1B |  | Median | 4 | [8 empty] | 1 |  |  | 1 |  | 8
33 | 196+145 | 196+235 |  | TCS 1B |  | Median | 4 | [11 empty] | 1 |  | 8
34 | 196+270 | 197+640 |  | TCS 6 |  | LHS/RHS Side |  | 22 | 22 |  | 8 | 8 |  | 22 | 22 |  | 16 | 10 |  | 2 | 88 |  | 16 | 88
35 | 197+650 | 197+740 |  | TCS 1B |  | Median | 4 | [11 empty] | 1 |  | 8
36 | 197+900 BUS BAY |  |  | TCS 2 |  | LHS Side/ RHS Side |  |  |  |  | 6 | 6 | [6 empty] | 2 |  |  |  |  | 12
37 | 199+710 | 199+800 |  | TCS 1B |  | Median | 4 | [8 empty] | 1 |  |  | 1 |  | 8
38 | 199+800 | 200+520 |  | TCS6 |  | LHS SIDE |  |  |  |  | 9 |  |  | 31 |  | 1 | 2 |  |  | 1 | 31 |  | 9 | 31
39 | 199+800 | 200+520 |  | TCS 5 |  | RHS SIDE |  |  | 22 | [8 empty] | 10 |  | 1 |  |  | 44
40 | 200+531 | 200+895 |  | TCS 1B |  | Median | 9 | [11 empty] | 1 |  | 18
41 | 200+895 | 201+100 |  |  |  | Median/LHS/RHS | 7 |  |  |  | 3 | 3 | [6 empty] | 1 | 1 |  |  | 14 | 6
42 | 201+260 BUS BAY |  |  | TCS 2 |  | LHS |  |  |  |  | 6 | [12 empty] | 6
43 | 201+654 | 201+760 |  | TCS 1B |  | Median | 5 | [8 empty] | 2 |  |  | 1 |  | 10
44 | 201+760 | 202+400 |  | TCS 6 |  | RHS/LHS SIDE |  |  |  |  | 6 | 6 |  | 18 | 18 |  | 6 | 10 |  | 2 | 36 |  | 12 | 36
45 | 202+400 | 202+490 |  | TCS 1B |  | Median | 4 | [11 empty] | 1 |  | 8
46 | 202+650 BUS BAY |  |  | TCS 2 |  | RHS | [5 empty] | 6 | [6 empty] | 1 |  |  |  |  | 6
47 | 205+900 BUS BAY |  |  | TCS 2 |  | LHS/RHS SIDE |  |  |  |  | 6 | 6 | [5 empty] | 20 | [5 empty] | 12
48 | 205+985 | 206+100 |  | TCS |  | RHS/LHS SIDE |  |  |  |  | 3 | 3 | [5 empty] | 20 |  |  |  |  | 6
49 | 206+100 | 206+350 |  | TCS 5 |  | RHS/LHS SIDE |  | 7 | 7 | [8 empty] | 10 | 1 | 1 |  |  | 14
50 | 206+350 | 206+415 |  | TCS |  | RHS/LHS SIDE |  |  |  |  | 3 | 3 | [5 empty] | 20 |  |  |  |  | 6
51 | 207+730 TRUCKLAY BAY |  |  | TCS 5 |  | LHS SIDE | 5 |  |  |  | 3 | 3 | [5 empty] | 20 |  |  |  |  | 16
52 | 207+630 BUS BAY |  |  | TCS 2 |  | RHS SIDE | [5 empty] | 6 | [6 empty] | 1 | 1 |  |  |  | 6
53 | 208+400 TRUCKLAY BAY |  |  | TCS 5 |  | RHS SIDE | 5 |  |  |  | 3 | 3 | [5 empty] | 20 | 1 |  |  |  | 16
54 | 209+300 BUS BAY |  |  | TCS 2 |  | LHS/RHS SIDE |  |  |  |  | 6 | 6 | [6 empty] | 2 |  |  |  |  | 12
55 | 209+310 | 209+400 |  | TCS 1B |  | Median | 4 | [13 empty] | 8
56 | 209+400 | 210+680 |  | TCS 6 |  | RHS SIDE |  |  | 8 | [11 empty] | 8 |  |  | 8
57 | 209+680 | 210+700 |  | TCS 6 |  | RHS/LHS SIDE | [7 empty] | 31 | 31 |  |  | 20 |  | 2 | 62 |  |  | 62
58 | 210+700 | 210+790 |  | TCS 1B |  | Median | 4 | [13 empty] | 8
59 | 211+200 BUS BAY |  |  | TCS 2 |  | LHS SIDE |  |  |  |  | 6 | 6 | [11 empty] | 12
60 | 211+285 | 211+420 |  |  |  | RHS/LHS SIDE |  |  |  |  | 4 | 4 | [5 empty] | 20 |  |  |  |  | 8
61 | 211+420 | 213+160 |  | TCS 5 |  | RHS/LHS SIDE |  |  |  |  | 6 |  |  | 55 | 55 |  |  | 30 | 1 | 3 |  |  | 226
62 | 213+160 | 214+430 |  | TCS 6 |  | RHS/LHS SIDE |  |  |  |  | 8 | 11 |  | 38 | 38 | 1 | 19 | 10 |  | 2 | 76 |  |  | 95
63 | 214+430 | 214+520 |  |  |  | RHS/LHS SIDE |  |  |  |  | 3 | 3 | [5 empty] | 20 | [5 empty] | 6
64 | 214+800 BUS BAY |  |  |  |  | RHS/LHS SIDE |  |  |  |  | 6 | 6 | [6 empty] | 1 | 1 |  |  |  | 12
65 | 215+600 BUS BAY |  |  | TCS 2 |  | RHS SIDE | [5 empty] | 6 | [6 empty] | 1 |  |  |  |  | 6
66 | 215+700 BUS BAY |  |  | TCS 2 |  | LHS SIDE |  |  |  |  | 6 | [7 empty] | 1 |  |  |  |  | 6
67 | 215+850 | 215+940 |  | TCS 1B |  | Median | 4 | [11 empty] | 1 |  | 8
68 | 215+940 | 216+820 |  | TCS 6 |  | RHS/LHS SIDE | [7 empty] | 25 | 25 |  |  | 10 |  | 2 | 50 |  |  | 50
69 | 216+820 | 216+910 |  | TCS 1B |  | Median | 3 | [11 empty] | 1 |  | 6
70 | 217+565 BUS BAY |  |  | TCS 2 |  | LHS/RHS Side |  |  |  |  | 6 | 6 | [6 empty] | 1 | 1 |  |  |  | 12
71 | 218+330 | 218+450 |  |  |  | RHS/LHS SIDE |  |  |  |  | 4 | 4 | [5 empty] | 20 |  |  |  |  | 8
72 | 218+450 | 218+800 |  | TCS 5 |  | RHS/LHS SIDE | [7 empty] | 11 | 11 |  |  | 10 | 1 | 1 |  |  | 44
73 | 218+811 | 218+930 |  |  |  | RHS/LHS SIDE |  |  |  |  | 4 | 4 | [5 empty] | 20 |  |  |  |  | 8
74 | 219+180 BUS BAY |  |  | TCS 2 |  | LHS SIDE |  |  |  |  | 6 | [7 empty] | 1 | 1 |  |  |  | 6
75 | 219+500 BUS BAY |  |  | TCS 2 |  | RHS SIDE | [5 empty] | 6 | [11 empty] | 6
TOTAL | [6 empty] | 97 | 212 | 217 | 0 | 205 | 273 | 0 | 398 | 288 | 27 | 109 | 545 | 40 | 45 | 889 | 116 | 916 | 940
[7 empty] | 526 |  |  |  | 478 |  |  | 686 | [6 empty] | 200914 | 22968 | 160300 | 141940
[5 empty] | Arm Type | Total Poles |  | 3c x 1.5 Sqmm Flexi cable
[5 empty] | Differential Arm poles | 686 |  | 8232 | 4459
[5 empty] | Double Arm Poles | 526 |  | 12624 | [12 empty] | 1921 | 21131
[5 empty] | Single Arm Poles | 478 |  | 5736
[5 empty] | VUP Lights | 142 |  | 1136
[5 empty] | Total Poles | 1690 |  | 27728 | 4459
[5 empty] | Total Illumanires | 2902 |  | 32187
Note on H33: Sri Kesari: As per site is 3 nos poles but one pole is missing
Note on H35: Sri Kesari: As per site inspection count is 3 nos poles medain but chainages is 4 nos
Note on J41: Sri Kesari: ACTUAL SIDE IS 31 NOS BUT COUNTING IS MISSING 9 NOS POLE

## VUP Flood Lights
VUP Locations With Detail BOQ
Sr.No | Chainage No | LHS/RHS | LENGTH | WIDTH | HEIGHT | No of Lights (50 W) | REMARK
1 | 173+100 | LHS | 20 | 15 | 6 | 9 | Refer VUP LUX design
2 | 175+380 | Median | 36 | 8 | 6 | 10 | Refer VUP LUX design
3 | 178+020 | LHS | 25 | 15 | 6 | 12 | Refer VUP LUX design
4 | 182+600 | Median | 29 | 10 | 6 | 10 | Refer VUP LUX design
5 | 193+090 | LHS | 20 | 15 | 6 | 9 | Refer VUP LUX design
6 | 194+780 | Median | 35 | 11 | 6 | 12 | Refer VUP LUX design
7 | 197+050 | Median | 24 | 33 | 5 | 18 | Refer VUP LUX design
8 | 200+150 | LHS | 24 | 15 | 6 | 12 | Refer VUP LUX design
9 | 202+150 | Median | 25 | 28 | 6 | 20 | Refer VUP LUX design
10 | 210+000 | Median | 10 | 30 | 6 | 10 | Refer VUP LUX design
11 | 213+740 | Median | 30 | 10 | 6 | 10 | Refer VUP LUX design
12 | 216+380 | Median | 30 | 10 | 6 | 10 | Refer VUP LUX design
[5 empty] | Total lights | 142 | Refer VUP LUX design

## Pole Damage
Nagalampalli to AP/KA Border - NH 4 (Mahasamudram Toll Plaza)
List of Damaged / Accident Poles - Highway Street Light Poles
S.No | Chainage | Side | Pole Installed at | Arm Type | Issue Type | Foundation | No of Poles | No of Lights | Comments
1 | 173230 | RHS | Service Road | Single Arm | Total Damage | Damaged | 1 | 1
2 | 173260 | RHS | Service Road | Single Arm | Total Damage | Damaged | 1 | 1
3 | 173450 | RHS | Service Road | Single Arm | Total Damage | Damaged | 1 | 1
4 | 173650 | LHS | MCW Shoulder | Single Arm | Accident Bend | Damaged | 1 | 1
5 | 173800 | RHS | MCW Shoulder | Single Arm | Total Damage | Damaged | 1 | 1
6 | 175200 | RHS | MCW Shoulder | Double Arm | Accident Bend | Damaged | 1 | 2
7 | 175400 | LHS | MCW Shoulder | Double Arm | Total Damage | Damaged | 1 | 2
8 | 182200 | LHS | MCW Shoulder | Double Arm | Accident Bend | Damaged | 1 | 2
9 | 185600 | Med | Median | Double Arm | Total Damage | Damaged | 1 | 2
10 | 185250 | Med | Median | Double Arm | Total Damage | Damaged | 1 | 2
11 | 185100 | Med | Median | Double Arm | Total Damage | Damaged | 1 | 2
12 | 181900 | LHS | MCW Shoulder | Double Arm | Accident Bend | Damaged | 1 | 2
13 | 191200 | RHS | MCW Shoulder | Single Arm | Accident Bend | Damaged | 1 | 1
14 | 191800 | RHS | MCW Shoulder | Single Arm | Total Damage | Damaged | 1 | 1
15 | 192020 | RHS | MCW Shoulder | Single Arm | Total Damage | Damaged | 1 | 1
16 | 192150 | LHS | Service Road | Single Arm | Total Damage | Damaged | 1 | 1
17 | 196300 | LHS | MCW Shoulder | Double Arm | Total Damage | Damaged | 1 | 2
18 | 197900 | LHS | MCW Shoulder | Single Arm | Total Damage | Damaged | 1 | 1
19 | 200850 | Med | Median | Double Arm | Total Damage | Damaged | 1 | 2
20 | 200900 | LHS | LHS | Double Arm | Total Damage | Damaged | 1 | 2
21 | 206100 | LHS | MCW Shoulder | Double Arm | Total Damage | Damaged | 1 | 2
22 | 207600 | Med | Median | Double Arm | Total Damage | Damaged | 1 | 2
23 | 208500 | RHS | MCW Shoulder | Double Arm | Total Damage | Damaged | 1 | 2
24 | 208530 | RHS | MCW Shoulder | Double Arm | Total Damage | Damaged | 1 | 2
25 | 207700 | LHS | MCW Shoulder | Double Arm | Total Damage | Damaged | 1 | 2
26 | 210350 | RHS | MCW Shoulder | Double Arm | Accident Bend | Damaged | 1 | 2
27 | 211150 | LHS | MCW Shoulder | Single Arm | Total Damage | Damaged | 1 | 1
28 | 212600 | RHS | MCW Shoulder | Double Arm | Total Damage | Damaged | 1 | 2
29 | 213300 | LHS | MCW Shoulder | Single Arm | Total Damage | Damaged | 1 | 1
30 | 214250 | LHS | MCW Shoulder | Double Arm | Total Damage | Damaged | 1 | 2
31 | 216800 | RHS | MCW Shoulder | Double Arm | Total Damage | Damaged | 1 | 2
32 | 217100 | LHS | MCW Shoulder | Single Arm | Total Damage | Damaged | 1 | 1
33 | 217200 | RHS | MCW Shoulder | Single Arm | Total Damage | Damaged | 1 | 1
34 | 218300 | LHS | MCW Shoulder | Single Arm | Accident Bend | Damaged | 1 | 1
35 | 219200 | LHS | MCW Shoulder | Single Arm | Accident Bend | Damaged | 1 | 1
Total Accidental Pole Damages/Missing to be repaired | [6 empty] | 35 | 54
[5 empty] | Total Single Arm Poles |  | 16
[5 empty] | Total Double Arm Poles |  | 19
[5 empty] | Total Poles |  | 35
[5 empty] | Total Lights |  | 54

## UG Cables & HDPE
| Chainage | [7 empty] | Poles
S.No | From | To | Feeder Pillar Location | Side | No of Cable Circuits | Pole Location | Arm Type | Cable Size | From | To | Total Poles | Pole to Pole Distance | Total Cable Qty | Additional Cable for Circuit Connection | Total Cable Qty | HDPE Pipe (Excavation & Trenching) | HDPE Ducting (VUP) | HDPE PCC Locations
1 | 172+430 | 173960 | 173+100 - In Btwn Pole no 14 and 15 | RHS | Circuit 1 | MCW Shoulder | SA | 25 Sqmm | 1 | 14 | 14 | 35 | 490 | 30 | 520 | 440
[6 empty] | Median | DA | 16 Sqmm | 1 | 4 | 4 | 35 | 140 | 25 | 165 | 125
[6 empty] | Bus Bay | SA | 10 Sqmm | 1 | 6 | 6 | 35 | 210 | 80 | 290 | 260
[5 empty] | Circuit 2 | MCW Shoulder | SA | 35 Sqmm | 15 | 36 | 22 | 35 | 770 | 0 | 770 | 730
[6 empty] | MCW Shoulder | SA | 35 Sqmm | 37 | 47 | 11 | 35 | 385 | 50 | 435 | 350
[6 empty] | MCW Shoulder | SA | 25 Sqmm | 48 | 53 | 6 | 35 | 210 | 30 | 240 | 190
2 | 172+430 | 173960 | 173+150 - In Btwn Pole 21 & 22 | LHS | Circuit 1 | MCW Shoulder | DA | 25 Sqmm | 10 | 21 | 12 | 35 | 420 | 30 | 450 |  | 450
[6 empty] | MCW Shoulder | DA | 16 Sqmm | 1 | 9 | 9 | 30 | 270 | 10 | 280 |  | 105 | 175
[5 empty] | Circuit 2 | Service Road | SA | 6 Sqmm | 1 | 7 | 7 | 35 | 245 | 50 | 295 | 265
[5 empty] | Circuit 3 | MCW Shoulder | DI | 35 Sqmm | 22 | 36 | 15 | 35 | 525 | 30 | 555 |  | 520
[6 empty] | MCW Shoulder | DI | 25 Sqmm | 37 | 42 | 6 | 35 | 210 | 0 | 210 |  | 190
[6 empty] | MCW Shoulder | SA | 25 Sqmm | 43 | 53 | 11 | 35 | 385 | 40 | 425 |  |  | 385
3 | 174765 | 175930 | 175+380 In Btwn Pole 17 & 18 | RHS | Circuit 1 | MCW Shoulder | DA | 35 Sqmm | 1 | 17 | 17 | 33 | 561 | 30 | 591 |  | 370 | 175
[6 empty] | Median | DA | 35 Sqmm | 1 | 5 | 5 | 36 | 180 | 0 | 180 | 160
[6 empty] | Bus Bay RHS | SA | 25 Sqmm | 1 | 6 | 6 | 35 | 210 | 30 | 240 | 180
[6 empty] | Bus Bay LHS | SA | 25 Sqmm | 1 | 6 | 6 | 35 | 210 | 30 | 240 | 180
[5 empty] | Circuit 2 | MCW Shoulder | DA | 10 Sqmm | 18 | 27 | 10 | 35 | 350 | 50 | 400 |  | 370
[6 empty] | MCW Shoulder | DA | 6 Sqmm | 28 | 31 | 4 | 35 | 140 | 0 | 140 |  |  | 140
4 | 174765 | 175930 | 175+380 In Btwn Pole 17 & 18 | LHS | Circuit 1 | MCW Shoulder | DA | 25 Sqmm | 1 | 17 | 17 | 33 | 561 | 30 | 591 |  | 360 | 175
[5 empty] | Circuit 2 | MCW Shoulder | DA | 16 Sqmm | 18 | 31 | 14 | 35 | 490 | 0 | 490 |  | 320 | 105
[6 empty] | Median | DA | 16 Sqmm | 32 | 35 | 4 | 30 | 120 | 0 | 120 | 105
5 | 177110 | 178630 | 178+020 in btwn Pole 34 & 35 | LHS | Circuit 1 | MCW Shoulder | DI | 50 Sqmm | 16 | 33 | 18 | 35 | 630 | 30 | 660 |  | 630
[6 empty] | MCW Shoulder | DA | 50 Sqmm | 6 | 15 | 10 | 35 | 350 | 0 | 350 |  |  | 350
[6 empty] | Median | DA | 35 Sqmm | 1 | 5 | 5 | 35 | 175 | 0 | 175 |  |  | 175
[5 empty] | Circuit 2 | MCW Shoulder | DI | 25 Sqmm | 34 | 42 | 9 | 35 | 315 | 30 | 345 |  | 320
[6 empty] | MCW Shoulder | DI | 16 Sqmm | 43 | 51 | 9 | 35 | 315 | 30 | 345 |  | 320
[5 empty] | Circuit 3 | Service Road | SA | 6 Sqmm | 1 | 9 | 9 | 35 | 315 | 30 | 345 | 300
6 | 177110 | 178630 | 178+080 in Btwn Pole 26 & 27 | RHS | Circuit 1 | MCW Shoulder | DI | 50 Sqmm | 15 | 26 | 12 | 35 | 420 | 25 | 445 |  | 430
[6 empty] | MCW Shoulder | DA | 35 Sqmm | 1 | 14 | 14 | 35 | 490 | 120 | 610 |  |  | 455
[6 empty] | Median | DA | 16 Sqmm | 1 | 4 | 4 | 35 | 140 | 0 | 140 | 125
[5 empty] | Circuit 2 | MCW Shoulder | DI | 25 Sqmm | 27 | 42 | 16 | 32.5 | 520 | 0 | 520 |  | 490
[6 empty] | MCW Shoulder | DI | 16 Sqmm | 43 | 51 | 9 | 35 | 315 | 0 | 315 |  | 280
[6 empty] | Bus Bay | SA | 6 Sqmm | 1 | 6 | 6 | 35 | 210 | 40 | 250 | 225
7 | 178630 | 179600 | 178+970 in Btwn pole 67 & 68 | LHS | Circuit 1 | MCW Shoulder | DI | 16 Sqmm | 52 | 66 | 15 | 35 | 525 | 65 | 590 |  | 570
[5 empty] | Circuit 2 | MCW Shoulder | DI | 25 Sqmm | 67 | 81 | 15 | 35 | 525 | 30 | 555 |  | 520
[6 empty] | Bus Bay | SA | 6 Sqmm | 1 | 6 | 6 | 35 | 210 | 0 | 210 | 190
8 | 178630 | 179600 | 178+970 in Btwn pole 67 & 68 | RHS | Circuit 1 | MCW Shoulder | DI | 16 Sqmm | 52 | 66 | 15 | 35 | 525 | 100 | 625 |  | 580
[5 empty] | Circuit 2 | MCW Shoulder | DI | 16 Sqmm | 67 | 81 | 15 | 35 | 525 | 60 | 585 |  | 530
9 | 179600 | 180540 | 180+100 in Btwn Pole 89 & 90 | RHS | Circuit 1 | MCW Shoulder | DI | 10 Sqmm | 82 | 88 | 7 | 33 | 231 | 0 | 231 | 190
[6 empty] | Bus Bay | SA | 10 Sqmm | 1 | 6 | 6 | 33 | 198 | 0 | 198 |  | 190
[5 empty] | Circuit 2 | MCW Shoulder | DI | 10 Sqmm | 89 | 99 | 11 | 35 | 385 | 25 | 410 |  | 380
[6 empty] | Service Road | SA | 6 Sqmm | 1 | 3 | 3 | 35 | 105 | 0 | 105 | 95
10 | 179600 | 180540 | 180+120 In Btwn Pole 102 & 103 | LHS | Circuit 1 | MCW Shoulder | DI | 25 Sqmm | 89 | 102 | 14 | 35 | 490 | 30 | 520 |  | 480
[6 empty] | MCW Shoulder | DI | 16 Sqmm | 82 | 88 | 7 | 35 | 245 | 0 | 245 |  | 215
[5 empty] | Circuit 2 | MCW Shoulder | DI | 10 Sqmm | 103 | 112 | 10 | 35 | 350 | 0 | 350 |  | 320
[6 empty] | Service Road | SA | 6 Sqmm | 1 | 3 | 3 | 35 | 105 | 40 | 145 | 125
11 | 181950 | 182840 | 182+650 in btwn Pole 17 & 18 | LHS | Circuit 1 | MCW Shoulder | DI | 25 Sqmm | 1 | 16 | 16 | 35 | 560 | 35 | 595 |  | 560
[6 empty] | Service Road | SA | 6 Sqmm | 1 | 5 | 5 | 35 | 175 | 5 | 180 | 170
[5 empty] | Circuit 2 | MCW Shoulder | SA | 6 Sqmm | 1 | 7 | 7 | 35 | 245 | 5 | 250 | 230
[5 empty] | Circuit 3 | MCW Shoulder | DI | 25 Sqmm | 17 | 34 | 18 | 35 | 630 | 0 | 630 |  | 290 | 315
12 | 181950 | 182840 | 182+650 in btwn Pole 17 & 18 | RHS | Circuit 1 | MCW Shoulder | DI | 25 Sqmm | 1 | 16 | 16 | 35 | 560 | 35 | 595 |  | 560
[6 empty] | Service Road | SA | 10 Sqmm | 1 | 5 | 5 | 35 | 175 | 0 | 175 | 160
[5 empty] | Circuit 2 | MCW Shoulder | SA | 6 Sqmm | 1 | 7 | 7 | 35 | 245 | 5 | 250 | 220
[5 empty] | Circuit 3 | MCW Shoulder | DI | 25 Sqmm | 17 | 34 | 18 | 35 | 630 | 0 | 630 |  | 290 | 315
13 | 182840 | 184100 | 183+630 at pole 47 | LHS | Circuit 1 | MCW Shoulder | DI | 16 Sqmm | 35 | 46 | 12 | 35 | 420 | 30 | 450 |  |  | 450
[6 empty] | Bus Bay | SA | 6 Sqmm | 1 | 6 | 6 | 35 | 210 | 5 | 215 | 195
[5 empty] | Circuit 2 | MCW Shoulder | DI | 16 Sqmm | 47 | 59 | 13 | 35 | 455 | 30 | 485 |  |  | 485
[5 empty] | Circuit 3 | Service Road | SA | 6 Sqmm | 1 | 3 | 3 | 35 | 105 | 30 | 135 | 125
14 | 182840 | 184100 | 183+630 at pole 47 | RHS | Circuit 1 | MCW Shoulder | DI | 10 Sqmm | 35 | 46 | 12 | 35 | 420 | 30 | 450 |  |  | 450
[5 empty] | Circuit 2 | MCW Shoulder | DI | 16 Sqmm | 47 | 59 | 13 | 35 | 455 | 30 | 485 |  |  | 485
[6 empty] | Service Road | SA | 6 Sqmm | 1 | 3 | 3 | 35 | 105 | 40 | 145 | 125
15 | 191971 | 192890 | 192+580 In Btwn Pole 19 & 20 | LHS | Circuit 1 | MCW Shoulder | DI | 35 Sqmm | 4 | 19 | 16 | 35 | 560 | 30 | 590 |  | 220 | 350
[6 empty] | MCW Shoulder | SA | 16 Sqmm | 1 | 3 | 3 | 35 | 105 | 0 | 105 | 90
[6 empty] | Median | DA | 10 Sqmm | 1 | 4 | 4 | 35 | 140 | 0 | 140 | 125
[5 empty] | Circuit 2 | MCW Shoulder | DI | 6 Sqmm | 20 | 28 | 9 | 35 | 315 | 30 | 345 |  | 320
[5 empty] | Circuit 3 | MCW Shoulder | SA | 10 Sqmm | 1 | 15 | 15 | 35 | 525 | 80 | 605 | 575
[5 empty] | Circuit 4 | MCW Shoulder | SA | 6 Sqmm | 16 | 27 | 12 | 35 | 420 | 80 | 500 | 470
16 | 192890 | 193580 | 193+060 in btwn 39 & 40 | LHS | Circuit 1 | MCW Shoulder | DI | 10 Sqmm | 29 | 40 | 12 | 35 | 420 | 0 | 420 |  | 390
[5 empty] | Circuit 2 | MCW Shoulder | DI | 25 Sqmm | 41 | 52 | 12 | 35 | 420 | 30 | 450 |  | 425
[6 empty] | MCW Shoulder | DI | 16 Sqmm | 53 | 58 | 6 | 35 | 210 | 0 | 210 |  | 190
[6 empty] | Median | DA | 10 Sqmm | 5 | 8 | 4 | 35 | 140 | 0 | 140 | 125
17 | 192890 | 193580 | 193+120 in Btwn 38 & 39 | RHS | Circuit 1 | MCW Shoulder | SA | 6 Sqmm | 28 | 39 | 12 | 35 | 420 | 30 | 450 | 425
[5 empty] | Circuit 2 | MCW Shoulder | SA | 10 Sqmm | 40 | 54 | 15 | 35 | 525 | 30 | 555 | 530
18 | 194150 | 194950 | 194+790 Btwn 22 & 23 | LHS | Circuit 1 | MCW Shoulder | DI | 25 Sqmm | 6 | 17 | 12 | 35 | 420 | 30 | 450 |  | 250 | 175
[6 empty] | MCW Shoulder | DI | 16 Sqmm | 1 | 5 | 5 | 35 | 175 | 0 | 175 |  |  | 175
[6 empty] | Median | DA | 16 Sqmm | 1 | 4 | 4 | 35 | 140 | 25 | 165 | 145
[5 empty] | Circuit 2 | MCW Shoulder | DI | 10 Sqmm | 18 | 29 | 12 | 35 | 420 | 30 | 450 |  | 425
19 | 194950 | 195790 | 194+950 in Btwn 27 & 28 | LHS | Circuit 1 | MCW Shoulder | DI | 25 Sqmm | 30 | 39 | 10 | 35 | 350 | 30 | 380 |  | 190 | 175
[6 empty] | MCW Shoulder | DI | 16 Sqmm | 40 | 45 | 6 | 35 | 210 | 0 | 210 |  |  | 210
[6 empty] | Median | DA | 10 Sqmm | 6 | 9 | 4 | 35 | 140 | 15 | 155 | 130
20 | 194150 | 194770 | 194+770 Btwn 17 & 18 | RHS | Circuit 1 | MCW Shoulder | DI | 35 Sqmm | 10 | 21 | 12 | 35 | 420 | 30 | 450 |  | 425
[6 empty] | MCW Shoulder | DI | 25 Sqmm | 1 | 9 | 9 | 35 | 315 | 105 | 420 |  |  | 420
21 | 194770 | 195790 | 194+770 Btwn 18 & 19 | RHS | Circuit 1 | MCW Shoulder | DI | 35 Sqmm | 22 | 33 | 12 | 35 | 420 | 135 | 555 |  | 520
[6 empty] | MCW Shoulder | DI | 35 Sqmm | 34 | 45 | 12 | 35 | 420 | 0 | 420 |  |  | 420
22 | 196145 | 197740 | 197+070 Btwn 24 & 25 | LHS | Circuit 1 | MCW Shoulder | DI | 35 Sqmm | 13 | 24 | 12 | 35 | 420 | 50 | 470 |  | 425
[6 empty] | MCW Shoulder | DI | 35 Sqmm | 1 | 12 | 12 | 35 | 420 | 0 | 420 |  |  | 420
[6 empty] | Median | DA | 25 Sqmm | 1 | 4 | 4 | 35 | 140 | 0 | 140 | 120
[5 empty] | Circuit 2 | MCW Shoulder | DI | 35 Sqmm | 25 | 36 | 12 | 35 | 420 | 30 | 450 |  | 435
[6 empty] | MCW Shoulder | DI | 35 Sqmm | 37 | 44 | 8 | 35 | 280 | 0 | 280 |  | 255
[6 empty] | Median | DA | 16 Sqmm | 5 | 8 | 4 | 35 | 140 | 0 | 140 | 120
[6 empty] | Bus Bay | SA | 16 Sqmm | 1 | 6 | 6 | 35 | 210 | 170 | 380 | 350
23 | 196145 | 197740 | 197+070 Btwn 24 & 25 | RHS | Circuit 1 | MCW Shoulder | DI | 35 Sqmm | 13 | 24 | 12 | 35 | 420 | 50 | 470 |  | 425
[6 empty] | MCW Shoulder | DI | 25 Sqmm | 1 | 12 | 12 | 35 | 420 | 70 | 490 |  |  | 420
[5 empty] | Circuit 2 | MCW Shoulder | DI | 25 Sqmm | 25 | 36 | 12 | 35 | 420 | 30 | 450 |  | 425
[6 empty] | MCW Shoulder | DI | 25 Sqmm | 37 | 44 | 8 | 35 | 280 | 0 | 280 |  | 255
[6 empty] | Bus Bay | SA | 16 Sqmm | 1 | 6 | 6 | 35 | 210 | 300 | 510 | 475
24 | 199710 | 200895 | 200+110 Btwn 14 & 15 | LHS | Circuit 1 | MCW Shoulder | DI | 25 Sqmm | 6 | 14 | 9 | 35 | 315 | 70 | 385 |  | 320
[6 empty] | MCW Shoulder | DI | 10 Sqmm | 1 | 5 | 5 | 35 | 175 | 0 | 175 |  | 145
[6 empty] | Median | DA | 10 Sqmm | 1 | 4 | 4 | 35 | 140 | 0 | 140 | 120
[5 empty] | Circuit 2 | MCW Shoulder | DI | 16 Sqmm | 15 | 26 | 12 | 35 | 420 | 30 | 450 |  | 425
[6 empty] | MCW Shoulder | DI | 16 Sqmm | 27 | 31 | 5 | 35 | 175 | 0 | 175 |  | 155
25 | 199710 | 200895 | 200250 Btwn 14 & 15 | RHS | Circuit 1 | MCW Shoulder | DI | 16 Sqmm | 1 | 15 | 15 | 35 | 525 | 30 | 555 |  | 515
[5 empty] | Circuit 2 | MCW Shoulder | DI | 25 Sqmm | 16 | 22 | 7 | 35 | 245 | 30 | 275 |  | 245
[6 empty] | Median | DA | 16 Sqmm | 5 | 13 | 9 | 35 | 315 | 60 | 375 | 355
26 | Truck lay bye | Bus Bay |  | LHS | Circuit 1 | MCW Shoulder | DA | 6 Sqmm | 1 | 4 | 4 | 35 | 140 | 45 | 185 | 165
[6 empty] | Service Road | SA | 6 Sqmm | 1 | 3 | 3 | 35 | 105 | 0 | 105 | 95
[6 empty] | Bus Bay | SA | 6 Sqmm | 1 | 6 | 6 | 35 | 210 | 110 | 320 | 310
| Truck lay bye | Bus Bay |  | RHS | Circuit 2 | MCW Shoulder | DA | 6 Sqmm | 1 | 4 | 4 | 35 | 140 | 5 | 145 | 130
[6 empty] | Service Road | SA | 6 Sqmm | 1 | 3 | 3 | 35 | 105 | 5 | 110 | 90
27 | 201654 | 202490 | 202+ 200 In Btwn 12 & 13 | LHS | Circuit 1 | MCW Shoulder | DI | 25 Sqmm | 7 | 12 | 6 | 35 | 210 | 30 | 240 |  | 220
[6 empty] | MCW Shoulder | DI | 16 Sqmm | 1 | 6 | 6 | 35 | 210 | 0 | 210 |  | 190
[6 empty] | Median | DA | 10 Sqmm | 1 | 5 | 5 | 35 | 175 | 60 | 235 | 215
[5 empty] | Circuit 2 | MCW Shoulder | DI | 10 Sqmm | 13 | 18 | 6 | 35 | 210 | 30 | 240 | 225
[6 empty] | Median | DA | 10 Sqmm | 6 | 9 | 4 | 35 | 140 | 30 | 170 | 150
28 | 201654 | 202490 | 202+ 200 In Btwn 12 & 13 | RHS | Circuit 1 | MCW Shoulder | DI | 10 Sqmm | 1 | 12 | 12 | 35 | 420 | 80 | 500 |  | 470
[5 empty] | Circuit 2 | MCW Shoulder | DI | 6 Sqmm | 13 | 18 | 6 | 35 | 210 | 80 | 290 |  | 260
[6 empty] | Bus Bay | SA | 6 Sqmm | 1 | 6 | 6 | 35 | 210 | 70 | 280 | 255
29 | 205980 | 206420 | 206+090 Btwn 12 & 13 | LHS | Circuit 1 | MCW Shoulder | DI | 10 Sqmm | 1 | 7 | 7 | 35 | 245 | 45 | 290 |  |  | 290
[6 empty] | Service Road | SA | 6 Sqmm | 1 | 3 | 3 | 35 | 105 | 5 | 110 | 95
[6 empty] | Bus Bay | SA | 6 Sqmm | 1 | 6 | 6 | 35 | 210 | 10 | 220 | 200
[6 empty] | Service Road | SA | 6 Sqmm | 5 | 6 | 2 | 35 | 70 | 40 | 110 | 95
[5 empty] | Circuit 2 | MCW Shoulder | DI | 10 Sqmm | 1 | 7 | 7 | 35 | 245 | 0 | 245 |  |  | 250
[6 empty] | Service Road | SA | 6 Sqmm | 1 | 3 | 3 | 35 | 105 | 5 | 110 | 95
[6 empty] | Bus Bay | SA | 6 Sqmm | 1 | 6 | 6 | 35 | 210 | 10 | 220 | 195
[6 empty] | Service Road | SA | 6 Sqmm | 5 | 6 | 2 | 35 | 70 | 45 | 115 | 95
30 | 209300 | 210790 | 210+000 Btwn 11 & 12 | LHS | Circuit 1 | MCW Shoulder | DI | 10 Sqmm | 1 | 12 | 12 | 35 | 420 | 0 | 420 |  |  | 425
[5 empty] | Circuit 2 | MCW Shoulder | DI | 16 Sqmm | 13 | 24 | 12 | 35 | 420 | 40 | 460 |  | 440
[6 empty] | MCW Shoulder | DI | 10 Sqmm | 25 | 31 | 7 | 35 | 245 | 0 | 245 |  | 270
[6 empty] | Median | DA | 10 Sqmm | 5 | 8 | 4 | 35 | 140 | 0 | 140 |  |  | 105
31 | 209300 | 210790 | 210+080 Btwn 21 & 22 | RHS | Circuit 1 | MCW Shoulder | DI | 50 Sqmm | 1 | 21 | 21 | 35 | 735 | 0 | 735 |  | 350 | 350
[6 empty] | Median | DA | 25 Sqmm | 1 | 4 | 4 | 35 | 140 | 70 | 210 | 130
[6 empty] | Bus Bay RHS | SA | 10 Sqmm | 1 | 6 | 6 | 35 | 210 | 15 | 225 | 200
[6 empty] | Bus Bay LHS | SA | 10 Sqmm | 1 | 6 | 6 | 35 | 210 | 15 | 225 | 200
[5 empty] | Circuit 2 | MCW Shoulder | DI | 25 Sqmm | 22 | 39 | 18 | 35 | 630 | 80 | 710 |  | 590
32 | 211200 | 212400 | 212+060 Btwn 20 & 21 | LHS | Circuit 1 | MCW Shoulder | DI | 35 Sqmm | 1 | 20 | 20 | 35 | 700 | 70 | 770 |  |  | 695
[6 empty] | Service Road | SA | 16 Sqmm | 1 | 4 | 4 | 35 | 140 | 5 | 145 | 125
[6 empty] | Bus Bay | SA | 16 Sqmm | 1 | 6 | 6 | 35 | 210 | 0 | 210 | 195
[5 empty] | Circuit 2 | MCW Shoulder | DI | 10 Sqmm | 21 | 32 | 12 | 35 | 420 | 0 | 420 |  |  | 415
33 | 211200 | 212400 | 212+100 Btwn 21 &22 | RHS | Circuit 1 | MCW Shoulder | DI | 35 Sqmm | 1 | 20 | 20 | 35 | 700 | 80 | 780 | 660
[6 empty] | Service Road | SA | 16 Sqmm | 1 | 4 | 4 | 35 | 140 | 0 | 140 | 130
[5 empty] | Circuit 2 | MCW Shoulder | DI | 10 Sqmm | 21 | 32 | 12 | 35 | 420 | 0 | 420 |  |  | 415
34 | 212400 | 213160 | 212+750 Btwn 43 &44 | LHS | Circuit 1 | MCW Shoulder | DI | 10 Sqmm | 33 | 44 | 12 | 35 | 420 | 30 | 450 |  |  | 450
|  |  |  | RHS | Circuit 2 | MCW Shoulder | DI | 10 Sqmm | 33 | 44 | 12 | 35 | 420 | 50 | 470 |  |  | 470
|  |  |  | LHS | Circuit 3 | MCW Shoulder | DI | 16 Sqmm | 45 | 55 | 11 | 35 | 385 | 260 | 645 |  |  | 645
|  |  |  | RHS | Circuit 4 | MCW Shoulder | DI | 10 Sqmm | 45 | 55 | 11 | 35 | 385 | 85 | 470 |  |  | 470
35 | 213170 | 214520 | 213+700 Btwn 17 &18 | LHS | Circuit 1 | MCW Shoulder | DI | 25 Sqmm | 1 | 18 | 18 | 35 | 630 | 30 | 660 |  |  | 660
[5 empty] | Circuit 2 | MCW Shoulder | DI | 25 Sqmm | 19 | 33 | 15 | 35 | 525 | 30 | 555 |  | 535
[6 empty] | MCW Shoulder | DA | 16 Sqmm | 34 | 38 | 5 | 35 | 175 | 0 | 175 |  |  | 175
[6 empty] | Service Road | SA | 16 Sqmm | 1 | 4 | 4 | 35 | 140 | 0 | 140 | 125
[5 empty] | Circuit 3 | Service Road | SA | 6 Sqmm | 1 | 8 | 8 | 35 | 280 | 0 | 280 | 255
36 | 213170 | 214520 | 213+700 Btwn 17 &18 | RHS | Circuit 1 | MCW Shoulder | DI | 25 Sqmm | 1 | 18 | 18 | 35 | 630 | 30 | 660 |  |  | 660
[5 empty] | Circuit 2 | MCW Shoulder | DI | 25 Sqmm | 19 | 33 | 15 | 35 | 525 | 30 | 555 |  | 535
[6 empty] | MCW Shoulder | DA | 16 Sqmm | 34 | 38 | 5 | 35 | 175 | 0 | 175 |  |  | 175
[6 empty] | Service Road | SA | 16 Sqmm | 1 | 4 | 4 | 35 | 140 | 0 | 140 | 130
[5 empty] | Circuit 3 | Service Road | SA | 6 Sqmm | 1 | 8 | 8 | 35 | 280 | 0 | 280 | 255
37 | 215860 | 216910 | 216+420 Btwn 15 & 16 | LHS | Circuit 1 | MCW Shoulder | DI | 35 Sqmm | 1 | 14 | 14 | 35 | 490 | 85 | 575 |  | 545
[6 empty] | Median | DA | 16 Sqmm | 1 | 4 | 4 | 35 | 140 | 15 | 155 |  | 135
[6 empty] | Bus Bay | SA | 16 Sqmm | 1 | 6 | 6 | 35 | 210 | 265 | 475 | 445
[5 empty] | Circuit 2 | MCW Shoulder | DI | 16 Sqmm | 15 | 25 | 11 | 35 | 385 | 160 | 545 |  | 525
38 | 215860 | 216910 | 216+420 Btwn 15 & 16 | RHS | Circuit 1 | MCW Shoulder | DI | 25 Sqmm | 1 | 15 | 15 | 35 | 525 | 65 | 590 |  | 560
[6 empty] | Bus Bay | SA | 16 Sqmm | 1 | 6 | 6 | 35 | 210 | 420 | 630 | 600
[5 empty] | Circuit 2 | MCW Shoulder | DI | 10 Sqmm | 16 | 25 | 10 | 35 | 350 | 135 | 485 |  | 480
39 | 218330 | 218920 | 218+600 Btwn 9 & 10 | LHS | Circuit 1 | Service Road | SA | 6 Sqmm | 1 | 4 | 4 | 35 | 140 | 0 | 140 |  |  | 145
[6 empty] | MCW Shoulder | DI | 6 Sqmm | 1 | 5 | 5 | 35 | 175 | 0 | 175 | 150
|  |  |  | LHS | Circuit 2 | MCW Shoulder | DI | 6 Sqmm | 6 | 11 | 6 | 35 | 210 | 0 | 210 | 200
[6 empty] | Service Road | SA | 6 Sqmm | 5 | 8 | 4 | 35 | 140 | 35 | 175 | 160
|  |  |  | RHS | Circuit 3 | Service Road | SA | 6 Sqmm | 1 | 4 | 4 | 35 | 140 | 0 | 140 | 160
[6 empty] | MCW Shoulder | DI | 6 Sqmm | 1 | 5 | 5 | 35 | 175 | 50 | 225 |  |  | 205
|  |  |  | RHS | Circuit 4 | MCW Shoulder | DI | 6 Sqmm | 6 | 11 | 6 | 35 | 210 | 40 | 250 | 240
[6 empty] | Service Road | SA | 6 Sqmm | 5 | 8 | 4 | 35 | 140 | 40 | 180 | 185
40 | 207730 | 208400 | New Feedar and proposed for both Bus Bay and Truck Lay Bye at 207+600 near RHS Bus Bay | LHS | Circuit 1 | MCW Shoulder | DA | 10 Sqmm | 1 | 5 | 5 | 35 | 175 | 120 | 295 |  |  | 295
[6 empty] | Service Road | SA | 6 Sqmm | 4 | 6 | 3 | 35 | 105 | 40 | 145 | 125
[6 empty] | Service Road | SA | 6 Sqmm | 4 | 6 | 3 | 35 | 105 | 40 | 145 | 125
|  |  |  | RHS | Circuit 2 | Bus Bay | SA | 16 Sqmm | 1 | 6 | 6 | 35 | 210 | 100 | 310 | 270
[6 empty] | MCW Shoulder | DA | 10 Sqmm | 1 | 5 | 5 | 35 | 175 | 120 | 295 |  |  | 295
[6 empty] | Service Road | SA | 6 Sqmm | 4 | 6 | 3 | 35 | 105 | 40 | 145 | 125
[6 empty] | Service Road | SA | 6 Sqmm | 4 | 6 | 3 | 35 | 105 | 40 | 145 | 125
41 | 184+540 | 184+760 | New Feeder at Bus Bays | LHS | Circuit 1 | Bus Bay | SA | 6 Sqmm | 1 | 6 | 6 | 35 | 210 | 180 | 390 | 340
|  |  |  | RHS | Circuit 2 | Bus Bay | SA | 6 Sqmm | 1 | 6 | 6 | 35 | 210 | 165 | 375 | 320
42 | 191+150 | 191500 | New Feeder at Bus Bays | LHS | Circuit 1 | Bus Bay | SA | 6 Sqmm | 1 | 6 | 6 | 35 | 210 | 180 | 390 | 320
|  |  |  | RHS | Circuit 2 | Bus Bay | SA | 6 Sqmm | 1 | 6 | 6 | 35 | 210 | 140 | 350 | 320
43 | 214+800 | 215+100 | New Feeder at Bus Bays | RHS | Circuit 1 | Bus Bay | SA | 6 Sqmm | 1 | 6 | 6 | 35 | 210 | 180 | 390 | 380
|  |  |  | LHS | Circuit 2 | Bus Bay | SA | 6 Sqmm | 1 | 6 | 6 | 35 | 210 | 220 | 430 | 320
[15 empty] | 63031 | 19340 | 24125 | 14990
Cable Mtrs
[6 empty] | UG Cable Size |  | Total |  |  | BOQ |  | Diff
[6 empty] | 6 Sqmm |  | 11240 |  |  | 11420 |  | 180
[6 empty] | 10 Sqmm |  | 11524 |  |  | 11525 |  | 1
[6 empty] | 16 Sqmm |  | 13325 |  |  | 13310 |  | -15
[6 empty] | 25 Sqmm |  | 15206 |  |  | 15305 |  | 99
[6 empty] | 35 Sqmm |  | 9546 |  |  | 9635 |  | 89
[6 empty] | 50 Sqmm |  | 2190 |  |  | 2190 |  | 0

## HDD
HDD Locations With HDPE Pipe Detail BOQ
Sr.No | Chainage No | No of HDD's | 50 MM HDPE pipe QTY (M) | REMARK
1 | 172+430 - 172+520 | 1 | 65
2 | 173+770 - 173+860 | 1 | 65
3 | 174+765 -174+855 | 1 | 65
4 | 175+870 175+930 | 1 | 65
5 | 177+110 - 177+200 | 1 | 65
6 | 184+540 BUS BAY | 1 | 65
7 | 191+150 BUS BAY | 6 | 390
8 | 191+971 - 192+061 | 1 | 65
9 | 193+500 -193+590 | 1 | 65
10 | 194+150 - 194+230 | 1 | 65
11 | 195+710 - 195+790 | 1 | 65
12 | 196+145 - 196+235 | 1 | 65
13 | 197+650 197+740 | 1 | 65
14 | 197+900 BUS BAY | 2 | 130
15 | 199+710 199+800 | 1 | 65
16 | 200+531 200+895 | 1 | 65
17 | 200+895 201+100 | 1 | 65
18 | 201+654 201+760 | 1 | 65
19 | 202+400 202+490 | 1 | 65
20 | 202+650 BUS BAY | 1 | 65
21 | 206+100 206+350 | 1 | 65
22 | 207+630 BUS BAY | 1 | 65
23 | 208+400 TRUCKLAY BAY | 1 | 65
24 | 209+300 BUS BAY | 2 | 130
25 | 211+420 - 213+160 | 1 | 65
26 | 214+800 BUS BAY | 1 | 65
27 | 215+600 BUS BAY | 1 | 65
28 | 215+700 BUS BAY | 1 | 65
29 | 215+850 215+940 | 1 | 65
30 | 216+820 - 216+910 | 1 | 65
31 | 217+565 BUS BAY | 1 | 65
32 | 218+450 - 218+800 | 1 | 65
33 | 219+180 BUS BAY | 1 | 65
| Total HDD Proposed | 40 | 2600

## Transformer List
Nagalampalli to AP/KA Border - NH 4 (Mahasamudram Toll Plaza)
Transformer Missing locations as per the site
S.No | Chainage | Side | Proposed Rating of a Transformer | Qty | Comments
1 | 184600 | LHS | 16KVA | 1
2 | 191350 | LHS | 16KVA | 1
3 | 205800 | RHS | 16KVA | 1 | Exisitng has Small 5 KVA Rating,So, New 16 KVA Transformer to be replaced
4 | 207600 | RHS | 16KVA | 1
5 | 214800 | LHS | 16KVA | 1
Transformer Missing locations |  |  |  | 5

## Arm Angle
Nagalampalli to AP/KA Border - NH 4 (Mahasamudram Toll Plaza)
Rectification of luminaire arm angle from the existing 5°/10° tilt angle to 0° tilt angle
Sr.No | Chainage No | LHS/RHS | No of Arms | REMARK
1 | 173+100 | LHS/RHS | 26
2 | 175+380 | LHS/RHS | 24
3 | 178+020 | LHS/RHS | 28
4 | 182+600 | LHS/RHS | 26
5 | 193+090 | LHS/RHS | 24
6 | 194+780 | LHS/RHS | 22
7 | 197+050 | LHS/RHS | 26
8 | 200+150 | LHS/RHS | 20
9 | 202+150 | LHS/RHS | 22
10 | 210+000 | LHS/RHS | 26
11 | 213+740 | LHS/RHS | 24
12 | 216+380 | LHS/RHS | 26
13 | 178+480 | RHS | 2
14 | 184+540 | LHS | 2
15 | 191+500 | LHS | 2
300

## Abstract (2)
S. No | Work Description | UOM | Total BOQ Qty | Removal Qty | Revised BOQ | Comments
5 | LTXPLE UG Cables , DWC Duct pipes
5.1 | Supply and laying of 4 C X 6 Sq. MM. XLPE insulated armoured cable of 1.1 KV grade as per IS 7098,(includeing end Termination of the cables with Lugs for all the cables and DC glands etc.) | Mtrs | 11240 | 2820 | 8420
5.2 | Supply and laying of 4 C X 10 Sq. MM. XLPE insulated armoured cable of 1.1 KV grade as per IS 7098,(includeing end Termination of the cables with Lugs for all the cables and DC glands etc.) | Mtrs | 11524 | 2015 | 9509
5.3 | Supply and laying of 4 C X 16 Sq. MM. XLPE insulated armoured cable of 1.1 KV grade as per IS 7098,(includeing end Termination of the cables with Lugs for all the cables and DC glands etc.) | Mtrs | 13325 | 1635 | 11690
5.4 | Supply and laying of 4 C X 25 Sq. MM. XLPE insulated armoured cable of 1.1 KV grade as per IS 7098,(includeing end Termination of the cables with Lugs for all the cables and DC glands etc.) | Mtrs | 15206 | 90 | 15116
5.5 | Supply and laying of 4 C X 35 Sq. MM. XLPE insulated armoured cable of 1.1 KV grade as per IS 7098,(includeing end Termination of the cables with Lugs for all the cables and DC glands etc.) | Mtrs | 9546 | 0 | 9546
5.6 | Supply and laying of 4 C X 50 Sq. MM. XLPE insulated armoured cable of 1.1 KV grade as per IS 7098,(includeing end Termination of the cables with Lugs for all the cables and DC glands etc.) | Mtrs | 2190 | 0 | 2190
5.7 | Supply and Laying of 3 C X 1.50 Sq. mm. Cu flexible wire cable of 1.1 KV grade as per IS 7098, .(include end Termination of the 3 C X 1.50 Sq. mm. Cu. Flexible cable with Lugs for all the cables including material ) | Mtrs | 32187 | 6300 | 25887
| Total Length of Cables proposed earlier |  | 95218 |  | 82358 | 12860
Revised length of UG Cables and Flexi cables |  |  | 82358

## 3C x 1.5 Sqmm
New 3C x 1.5 Sqmm Copper Flexible Cable for LED Lights | [7 empty] | Old 2C x 1.5 Sqmm Copper Flexible Cable - Existing HPSV
S.No | Arm Type | Total Poles | No of Lights in Arm | Length for Each poles | Total Length | Second Light Arm Length | Total Mtrs | S.No | Arm Type | Working Qty | No of Lights in Arm | Length for Each poles | Total Length
1 | Differential Arm poles | 686 | 2 | 12 | 8232 | 6.5 | 4459 | 1 | Differential Arm poles | 185 | 2 | 12 | 2220
2 | Double Arm Poles | 526 | 2 | 12 | 12624 |  |  | 2 | Double Arm Poles | 295 | 2 | 12 | 7080
3 | Single Arm Poles | 478 | 1 | 12 | 5736 |  |  | 3 | Single Arm Poles | 275 | 1 | 12 | 3300
4 | VUP Lights | 142 | 1 | 8 | 1136
Total |  |  |  |  | 27728 |  | 4459 | [5 empty] | 12600
Total Length of 3C x 1.5 Sqmm Cable |  |  |  |  | 32187 |  |  | Total Length of old 2C x 1.5 sqmmcable can be Re-Used |  |  |  |  | 6300
Note on O10: Ganesh Kumar K: For Each Light, We need to Use 24 Mtrs, bcoz its only 2C, we need 3C.

## UG Cables & HDPE (2)
BOQ for New UG Cable across each and Every Stretch
S.No | Chainage |  | Feeder Pillar Location | Side | No of Cable Circuits | Pole Location | Arm Type | Cable Size | Poles |  | Total Poles | Pole to Pole Distance | Total Cable Qty | Additional Cable for Circuit Connection | Total Cable Qty | HDPE Pipe (Excavation & Trenching) | HDPE Ducting (VUP) | HDPE PCC Locations
| From | To | [6 empty] | From | To
1 | 172+430 | 173960 | 173+100 - In Btwn Pole no 14 and 15 | RHS | Circuit 1 | MCW Shoulder | SA | 25 Sqmm | 1 | 14 | 14 | 35 | 490 | 30 | 520 | 440
[6 empty] | Median | DA | 16 Sqmm | 1 | 4 | 4 | 35 | 140 | 25 | 165 | 125
[6 empty] | Bus Bay | SA | 10 Sqmm | 1 | 6 | 6 | 35 | 210 | 80 | 290 | 260
[5 empty] | Circuit 2 | MCW Shoulder | SA | 35 Sqmm | 15 | 36 | 22 | 35 | 770 | 0 | 770 | 730
[6 empty] | MCW Shoulder | SA | 35 Sqmm | 37 | 47 | 11 | 35 | 385 | 50 | 435 | 350
[6 empty] | MCW Shoulder | SA | 25 Sqmm | 48 | 53 | 6 | 35 | 210 | 30 | 240 | 190
2 | 172+430 | 173960 | 173+150 - In Btwn Pole 21 & 22 | LHS | Circuit 1 | MCW Shoulder | DA | 25 Sqmm | 10 | 21 | 12 | 35 | 420 | 30 | 450 |  | 450
[6 empty] | MCW Shoulder | DA | 16 Sqmm | 1 | 9 | 9 | 30 | 270 | 10 | 280 |  | 105 | 175
[5 empty] | Circuit 2 | Service Road | SA | 6 Sqmm | 1 | 7 | 7 | 35 | 245 | 50 | 295 | 265
[5 empty] | Circuit 3 | MCW Shoulder | DI | 35 Sqmm | 22 | 36 | 15 | 35 | 525 | 30 | 555 |  | 520
[6 empty] | MCW Shoulder | DI | 25 Sqmm | 37 | 42 | 6 | 35 | 210 | 0 | 210 |  | 190
[6 empty] | MCW Shoulder | SA | 25 Sqmm | 43 | 53 | 11 | 35 | 385 | 40 | 425 |  |  | 385
3 | 174765 | 175930 | 175+380 In Btwn Pole 17 & 18 | RHS | Circuit 1 | MCW Shoulder | DA | 35 Sqmm | 1 | 17 | 17 | 33 | 561 | 30 | 591 |  | 370 | 175
[6 empty] | Median | DA | 35 Sqmm | 1 | 5 | 5 | 36 | 180 | 0 | 180 | 160
[6 empty] | Bus Bay RHS | SA | 25 Sqmm | 1 | 6 | 6 | 35 | 210 | 30 | 240 | 180
[6 empty] | Bus Bay LHS | SA | 25 Sqmm | 1 | 6 | 6 | 35 | 210 | 30 | 240 | 180
[5 empty] | Circuit 2 | MCW Shoulder | DA | 10 Sqmm | 18 | 27 | 10 | 35 | 350 | 50 | 400 |  | 370
[6 empty] | MCW Shoulder | DA | 6 Sqmm | 28 | 31 | 4 | 35 | 140 | 0 | 140 |  |  | 140
4 | 174765 | 175930 | 175+380 In Btwn Pole 17 & 18 | LHS | Circuit 1 | MCW Shoulder | DA | 25 Sqmm | 1 | 17 | 17 | 33 | 561 | 30 | 591 |  | 360 | 175
[5 empty] | Circuit 2 | MCW Shoulder | DA | 16 Sqmm | 18 | 31 | 14 | 35 | 490 | 0 | 490 |  | 320 | 105
[6 empty] | Median | DA | 16 Sqmm | 32 | 35 | 4 | 30 | 120 | 0 | 120 | 105
5 | 177110 | 178630 | 178+020 in btwn Pole 34 & 35 | LHS | Circuit 1 | MCW Shoulder | DI | 50 Sqmm | 16 | 33 | 18 | 35 | 630 | 30 | 660 |  | 630
[6 empty] | MCW Shoulder | DA | 50 Sqmm | 6 | 15 | 10 | 35 | 350 | 0 | 350 |  |  | 350
[6 empty] | Median | DA | 35 Sqmm | 1 | 5 | 5 | 35 | 175 | 0 | 175 |  |  | 175
[5 empty] | Circuit 2 | MCW Shoulder | DI | 25 Sqmm | 34 | 42 | 9 | 35 | 315 | 30 | 345 |  | 320
[6 empty] | MCW Shoulder | DI | 16 Sqmm | 43 | 51 | 9 | 35 | 315 | 30 | 345 |  | 320
[5 empty] | Circuit 3 | Service Road | SA | 6 Sqmm | 1 | 9 | 9 | 35 | 315 | 30 | 345 | 300
6 | 177110 | 178630 | 178+080 in Btwn Pole 26 & 27 | RHS | Circuit 1 | MCW Shoulder | DI | 50 Sqmm | 15 | 26 | 12 | 35 | 420 | 25 | 445 |  | 430
[6 empty] | MCW Shoulder | DA | 35 Sqmm | 1 | 14 | 14 | 35 | 490 | 120 | 610 |  |  | 455
[6 empty] | Median | DA | 16 Sqmm | 1 | 4 | 4 | 35 | 140 | 0 | 140 | 125
[5 empty] | Circuit 2 | MCW Shoulder | DI | 25 Sqmm | 27 | 42 | 16 | 32.5 | 520 | 0 | 520 |  | 490
[6 empty] | MCW Shoulder | DI | 16 Sqmm | 43 | 51 | 9 | 35 | 315 | 0 | 315 |  | 280
[6 empty] | Bus Bay | SA | 6 Sqmm | 1 | 6 | 6 | 35 | 210 | 40 | 250 | 225
7 | 178630 | 179600 | 178+970 in Btwn pole 67 & 68 | LHS | Circuit 1 | MCW Shoulder | DI | 16 Sqmm | 52 | 66 | 15 | 35 | 525 | 65 | 590 |  | 570
[5 empty] | Circuit 2 | MCW Shoulder | DI | 25 Sqmm | 67 | 81 | 15 | 35 | 525 | 30 | 555 |  | 520
[6 empty] | Bus Bay | SA | 6 Sqmm | 1 | 6 | 6 | 35 | 210 | 0 | 210 | 190
8 | 178630 | 179600 | 178+970 in Btwn pole 67 & 68 | RHS | Circuit 1 | MCW Shoulder | DI | 16 Sqmm | 52 | 66 | 15 | 35 | 525 | 100 | 625 |  | 580
[5 empty] | Circuit 2 | MCW Shoulder | DI | 16 Sqmm | 67 | 81 | 15 | 35 | 525 | 60 | 585 |  | 530
9 | 179600 | 180540 | 180+100 in Btwn Pole 89 & 90 | RHS | Circuit 1 | MCW Shoulder | DI | 10 Sqmm | 82 | 88 | 7 | 33 | 231 | 0 | 231 | 190
[6 empty] | Bus Bay | SA | 10 Sqmm | 1 | 6 | 6 | 33 | 198 | 0 | 198 |  | 190
[5 empty] | Circuit 2 | MCW Shoulder | DI | 10 Sqmm | 89 | 99 | 11 | 35 | 385 | 25 | 410 |  | 380
[6 empty] | Service Road | SA | 6 Sqmm | 1 | 3 | 3 | 35 | 105 | 0 | 105 | 95
10 | 179600 | 180540 | 180+120 In Btwn Pole 102 & 103 | LHS | Circuit 1 | MCW Shoulder | DI | 25 Sqmm | 89 | 102 | 14 | 35 | 490 | 30 | 520 |  | 480
[6 empty] | MCW Shoulder | DI | 16 Sqmm | 82 | 88 | 7 | 35 | 245 | 0 | 245 |  | 215
[5 empty] | Circuit 2 | MCW Shoulder | DI | 10 Sqmm | 103 | 112 | 10 | 35 | 350 | 0 | 350 |  | 320
[6 empty] | Service Road | SA | 6 Sqmm | 1 | 3 | 3 | 35 | 105 | 40 | 145 | 125
11 | 181950 | 182840 | 182+650 in btwn Pole 17 & 18 | LHS | Circuit 1 | MCW Shoulder | DI | 25 Sqmm | 1 | 16 | 16 | 35 | 560 | 35 | 595 |  | 560
[6 empty] | Service Road | SA | 6 Sqmm | 1 | 5 | 5 | 35 | 175 | 5 | 180 | 170
[5 empty] | Circuit 2 | MCW Shoulder | SA | 6 Sqmm | 1 | 7 | 7 | 35 | 245 | 5 | 250 | 230
[5 empty] | Circuit 3 | MCW Shoulder | DI | 25 Sqmm | 17 | 34 | 18 | 35 | 630 | 0 | 630 |  | 290 | 315
12 | 181950 | 182840 | 182+650 in btwn Pole 17 & 18 | RHS | Circuit 1 | MCW Shoulder | DI | 25 Sqmm | 1 | 16 | 16 | 35 | 560 | 35 | 595 |  | 560
[6 empty] | Service Road | SA | 10 Sqmm | 1 | 5 | 5 | 35 | 175 | 0 | 175 | 160
[5 empty] | Circuit 2 | MCW Shoulder | SA | 6 Sqmm | 1 | 7 | 7 | 35 | 245 | 5 | 250 | 220
[5 empty] | Circuit 3 | MCW Shoulder | DI | 25 Sqmm | 17 | 34 | 18 | 35 | 630 | 0 | 630 |  | 290 | 315
13 | 182840 | 184100 | 183+630 at pole 47 | LHS | Circuit 1 | MCW Shoulder | DI | 16 Sqmm | 35 | 46 | 12 | 35 | 420 | 30 | 450 |  |  | 450
[6 empty] | Bus Bay | SA | 6 Sqmm | 1 | 6 | 6 | 35 | 210 | 5 | 215 | 195
[5 empty] | Circuit 2 | MCW Shoulder | DI | 16 Sqmm | 47 | 59 | 13 | 35 | 455 | 30 | 485 |  |  | 485
[5 empty] | Circuit 3 | Service Road | SA | 6 Sqmm | 1 | 3 | 3 | 35 | 105 | 30 | 135 | 125
14 | 182840 | 184100 | 183+630 at pole 47 | RHS | Circuit 1 | MCW Shoulder | DI | 10 Sqmm | 35 | 46 | 12 | 35 | 420 | 30 | 450 |  |  | 450
[5 empty] | Circuit 2 | MCW Shoulder | DI | 16 Sqmm | 47 | 59 | 13 | 35 | 455 | 30 | 485 |  |  | 485
[6 empty] | Service Road | SA | 6 Sqmm | 1 | 3 | 3 | 35 | 105 | 40 | 145 | 125
15 | 191971 | 192890 | 192+580 In Btwn Pole 19 & 20 | LHS | Circuit 1 | MCW Shoulder | DI | 35 Sqmm | 4 | 19 | 16 | 35 | 560 | 30 | 590 |  | 220 | 350
[6 empty] | MCW Shoulder | SA | 16 Sqmm | 1 | 3 | 3 | 35 | 105 | 0 | 105 | 90
[6 empty] | Median | DA | 10 Sqmm | 1 | 4 | 4 | 35 | 140 | 0 | 140 | 125
[5 empty] | Circuit 2 | MCW Shoulder | DI | 6 Sqmm | 20 | 28 | 9 | 35 | 315 | 30 | 345 |  | 320
[5 empty] | Circuit 3 | MCW Shoulder | SA | 10 Sqmm | 1 | 15 | 15 | 35 | 525 | 80 | 605 | 575
[5 empty] | Circuit 4 | MCW Shoulder | SA | 6 Sqmm | 16 | 27 | 12 | 35 | 420 | 80 | 500 | 470
16 | 192890 | 193580 | 193+060 in btwn 39 & 40 | LHS | Circuit 1 | MCW Shoulder | DI | 10 Sqmm | 29 | 40 | 12 | 35 | 420 | 0 | 420 |  | 390
[5 empty] | Circuit 2 | MCW Shoulder | DI | 25 Sqmm | 41 | 52 | 12 | 35 | 420 | 30 | 450 |  | 425
[6 empty] | MCW Shoulder | DI | 16 Sqmm | 53 | 58 | 6 | 35 | 210 | 0 | 210 |  | 190
[6 empty] | Median | DA | 10 Sqmm | 5 | 8 | 4 | 35 | 140 | 0 | 140 | 125
17 | 192890 | 193580 | 193+120 in Btwn 38 & 39 | RHS | Circuit 1 | MCW Shoulder | SA | 6 Sqmm | 28 | 39 | 12 | 35 | 420 | 30 | 450 | 425
[5 empty] | Circuit 2 | MCW Shoulder | SA | 10 Sqmm | 40 | 54 | 15 | 35 | 525 | 30 | 555 | 530
18 | 194150 | 194950 | 194+790 Btwn 22 & 23 | LHS | Circuit 1 | MCW Shoulder | DI | 25 Sqmm | 6 | 17 | 12 | 35 | 420 | 30 | 450 |  | 250 | 175
[6 empty] | MCW Shoulder | DI | 16 Sqmm | 1 | 5 | 5 | 35 | 175 | 0 | 175 |  |  | 175
[6 empty] | Median | DA | 16 Sqmm | 1 | 4 | 4 | 35 | 140 | 25 | 165 | 145
[5 empty] | Circuit 2 | MCW Shoulder | DI | 10 Sqmm | 18 | 29 | 12 | 35 | 420 | 30 | 450 |  | 425
19 | 194950 | 195790 | 194+950 in Btwn 27 & 28 | LHS | Circuit 1 | MCW Shoulder | DI | 25 Sqmm | 30 | 39 | 10 | 35 | 350 | 30 | 380 |  | 190 | 175
[6 empty] | MCW Shoulder | DI | 16 Sqmm | 40 | 45 | 6 | 35 | 210 | 0 | 210 |  |  | 210
[6 empty] | Median | DA | 10 Sqmm | 6 | 9 | 4 | 35 | 140 | 15 | 155 | 130
20 | 194150 | 194770 | 194+770 Btwn 17 & 18 | RHS | Circuit 1 | MCW Shoulder | DI | 35 Sqmm | 10 | 21 | 12 | 35 | 420 | 30 | 450 |  | 425
[6 empty] | MCW Shoulder | DI | 25 Sqmm | 1 | 9 | 9 | 35 | 315 | 105 | 420 |  |  | 420
21 | 194770 | 195790 | 194+770 Btwn 18 & 19 | RHS | Circuit 1 | MCW Shoulder | DI | 35 Sqmm | 22 | 33 | 12 | 35 | 420 | 135 | 555 |  | 520
[6 empty] | MCW Shoulder | DI | 35 Sqmm | 34 | 45 | 12 | 35 | 420 | 0 | 420 |  |  | 420
22 | 196145 | 197740 | 197+070 Btwn 24 & 25 | LHS | Circuit 1 | MCW Shoulder | DI | 35 Sqmm | 13 | 24 | 12 | 35 | 420 | 50 | 470 |  | 425
[6 empty] | MCW Shoulder | DI | 35 Sqmm | 1 | 12 | 12 | 35 | 420 | 0 | 420 |  |  | 420
[6 empty] | Median | DA | 25 Sqmm | 1 | 4 | 4 | 35 | 140 | 0 | 140 | 120
[5 empty] | Circuit 2 | MCW Shoulder | DI | 35 Sqmm | 25 | 36 | 12 | 35 | 420 | 30 | 450 |  | 435
[6 empty] | MCW Shoulder | DI | 35 Sqmm | 37 | 44 | 8 | 35 | 280 | 0 | 280 |  | 255
[6 empty] | Median | DA | 16 Sqmm | 5 | 8 | 4 | 35 | 140 | 0 | 140 | 120
[6 empty] | Bus Bay | SA | 16 Sqmm | 1 | 6 | 6 | 35 | 210 | 170 | 380 | 350
23 | 196145 | 197740 | 197+070 Btwn 24 & 25 | RHS | Circuit 1 | MCW Shoulder | DI | 35 Sqmm | 13 | 24 | 12 | 35 | 420 | 50 | 470 |  | 425
[6 empty] | MCW Shoulder | DI | 25 Sqmm | 1 | 12 | 12 | 35 | 420 | 70 | 490 |  |  | 420
[5 empty] | Circuit 2 | MCW Shoulder | DI | 25 Sqmm | 25 | 36 | 12 | 35 | 420 | 30 | 450 |  | 425
[6 empty] | MCW Shoulder | DI | 25 Sqmm | 37 | 44 | 8 | 35 | 280 | 0 | 280 |  | 255
[6 empty] | Bus Bay | SA | 16 Sqmm | 1 | 6 | 6 | 35 | 210 | 300 | 510 | 475
24 | 199710 | 200895 | 200+110 Btwn 14 & 15 | LHS | Circuit 1 | MCW Shoulder | DI | 25 Sqmm | 6 | 14 | 9 | 35 | 315 | 70 | 385 |  | 320
[6 empty] | MCW Shoulder | DI | 10 Sqmm | 1 | 5 | 5 | 35 | 175 | 0 | 175 |  | 145
[6 empty] | Median | DA | 10 Sqmm | 1 | 4 | 4 | 35 | 140 | 0 | 140 | 120
[5 empty] | Circuit 2 | MCW Shoulder | DI | 16 Sqmm | 15 | 26 | 12 | 35 | 420 | 30 | 450 |  | 425
[6 empty] | MCW Shoulder | DI | 16 Sqmm | 27 | 31 | 5 | 35 | 175 | 0 | 175 |  | 155
25 | 199710 | 200895 | 200250 Btwn 14 & 15 | RHS | Circuit 1 | MCW Shoulder | DI | 16 Sqmm | 1 | 15 | 15 | 35 | 525 | 30 | 555 |  | 515
[5 empty] | Circuit 2 | MCW Shoulder | DI | 25 Sqmm | 16 | 22 | 7 | 35 | 245 | 30 | 275 |  | 245
[6 empty] | Median | DA | 16 Sqmm | 5 | 13 | 9 | 35 | 315 | 60 | 375 | 355
26 | Truck lay bye | Bus Bay |  | LHS | Circuit 1 | MCW Shoulder | DA | 6 Sqmm | 1 | 4 | 4 | 35 | 140 | 45 | 185 | 165
[6 empty] | Service Road | SA | 6 Sqmm | 1 | 3 | 3 | 35 | 105 | 0 | 105 | 95
[6 empty] | Bus Bay | SA | 6 Sqmm | 1 | 6 | 6 | 35 | 210 | 110 | 320 | 310
| Truck lay bye | Bus Bay |  | RHS | Circuit 2 | MCW Shoulder | DA | 6 Sqmm | 1 | 4 | 4 | 35 | 140 | 5 | 145 | 130
[6 empty] | Service Road | SA | 6 Sqmm | 1 | 3 | 3 | 35 | 105 | 5 | 110 | 90
27 | 201654 | 202490 | 202+ 200 In Btwn 12 & 13 | LHS | Circuit 1 | MCW Shoulder | DI | 25 Sqmm | 7 | 12 | 6 | 35 | 210 | 30 | 240 |  | 220
[6 empty] | MCW Shoulder | DI | 16 Sqmm | 1 | 6 | 6 | 35 | 210 | 0 | 210 |  | 190
[6 empty] | Median | DA | 10 Sqmm | 1 | 5 | 5 | 35 | 175 | 60 | 235 | 215
[5 empty] | Circuit 2 | MCW Shoulder | DI | 10 Sqmm | 13 | 18 | 6 | 35 | 210 | 30 | 240 | 225
[6 empty] | Median | DA | 10 Sqmm | 6 | 9 | 4 | 35 | 140 | 30 | 170 | 150
28 | 201654 | 202490 | 202+ 200 In Btwn 12 & 13 | RHS | Circuit 1 | MCW Shoulder | DI | 10 Sqmm | 1 | 12 | 12 | 35 | 420 | 80 | 500 |  | 470
[5 empty] | Circuit 2 | MCW Shoulder | DI | 6 Sqmm | 13 | 18 | 6 | 35 | 210 | 80 | 290 |  | 260
[6 empty] | Bus Bay | SA | 6 Sqmm | 1 | 6 | 6 | 35 | 210 | 70 | 280 | 255
29 | 205980 | 206420 | 206+090 Btwn 12 & 13 | LHS | Circuit 1 | MCW Shoulder | DI | 10 Sqmm | 1 | 7 | 7 | 35 | 245 | 45 | 290 |  |  | 290
[6 empty] | Service Road | SA | 6 Sqmm | 1 | 3 | 3 | 35 | 105 | 5 | 110 | 95
[6 empty] | Bus Bay | SA | 6 Sqmm | 1 | 6 | 6 | 35 | 210 | 10 | 220 | 200
[6 empty] | Service Road | SA | 6 Sqmm | 5 | 6 | 2 | 35 | 70 | 40 | 110 | 95
[5 empty] | Circuit 2 | MCW Shoulder | DI | 10 Sqmm | 1 | 7 | 7 | 35 | 245 | 0 | 245 |  |  | 250
[6 empty] | Service Road | SA | 6 Sqmm | 1 | 3 | 3 | 35 | 105 | 5 | 110 | 95
[6 empty] | Bus Bay | SA | 6 Sqmm | 1 | 6 | 6 | 35 | 210 | 10 | 220 | 195
[6 empty] | Service Road | SA | 6 Sqmm | 5 | 6 | 2 | 35 | 70 | 45 | 115 | 95
30 | 209300 | 210790 | 210+000 Btwn 11 & 12 | LHS | Circuit 1 | MCW Shoulder | DI | 10 Sqmm | 1 | 12 | 12 | 35 | 420 | 0 | 420 |  |  | 425
[5 empty] | Circuit 2 | MCW Shoulder | DI | 16 Sqmm | 13 | 24 | 12 | 35 | 420 | 40 | 460 |  | 440
[6 empty] | MCW Shoulder | DI | 10 Sqmm | 25 | 31 | 7 | 35 | 245 | 0 | 245 |  | 270
[6 empty] | Median | DA | 10 Sqmm | 5 | 8 | 4 | 35 | 140 | 0 | 140 |  |  | 105
31 | 209300 | 210790 | 210+080 Btwn 21 & 22 | RHS | Circuit 1 | MCW Shoulder | DI | 50 Sqmm | 1 | 21 | 21 | 35 | 735 | 0 | 735 |  | 350 | 350
[6 empty] | Median | DA | 25 Sqmm | 1 | 4 | 4 | 35 | 140 | 70 | 210 | 130
[6 empty] | Bus Bay RHS | SA | 10 Sqmm | 1 | 6 | 6 | 35 | 210 | 15 | 225 | 200
[6 empty] | Bus Bay LHS | SA | 10 Sqmm | 1 | 6 | 6 | 35 | 210 | 15 | 225 | 200
[5 empty] | Circuit 2 | MCW Shoulder | DI | 25 Sqmm | 22 | 39 | 18 | 35 | 630 | 80 | 710 |  | 590
32 | 211200 | 212400 | 212+060 Btwn 20 & 21 | LHS | Circuit 1 | MCW Shoulder | DI | 35 Sqmm | 1 | 20 | 20 | 35 | 700 | 70 | 770 |  |  | 695
[6 empty] | Service Road | SA | 16 Sqmm | 1 | 4 | 4 | 35 | 140 | 5 | 145 | 125
[6 empty] | Bus Bay | SA | 16 Sqmm | 1 | 6 | 6 | 35 | 210 | 0 | 210 | 195
[5 empty] | Circuit 2 | MCW Shoulder | DI | 10 Sqmm | 21 | 32 | 12 | 35 | 420 | 0 | 420 |  |  | 415
33 | 211200 | 212400 | 212+100 Btwn 21 &22 | RHS | Circuit 1 | MCW Shoulder | DI | 35 Sqmm | 1 | 20 | 20 | 35 | 700 | 80 | 780 | 660
[6 empty] | Service Road | SA | 16 Sqmm | 1 | 4 | 4 | 35 | 140 | 0 | 140 | 130
[5 empty] | Circuit 2 | MCW Shoulder | DI | 10 Sqmm | 21 | 32 | 12 | 35 | 420 | 0 | 420 |  |  | 415
34 | 212400 | 213160 | 212+750 Btwn 43 &44 | LHS | Circuit 1 | MCW Shoulder | DI | 10 Sqmm | 33 | 44 | 12 | 35 | 420 | 30 | 450 |  |  | 450
|  |  |  | RHS | Circuit 2 | MCW Shoulder | DI | 10 Sqmm | 33 | 44 | 12 | 35 | 420 | 50 | 470 |  |  | 470
|  |  |  | LHS | Circuit 3 | MCW Shoulder | DI | 16 Sqmm | 45 | 55 | 11 | 35 | 385 | 260 | 645 |  |  | 645
|  |  |  | RHS | Circuit 4 | MCW Shoulder | DI | 10 Sqmm | 45 | 55 | 11 | 35 | 385 | 85 | 470 |  |  | 470
35 | 213170 | 214520 | 213+700 Btwn 17 &18 | LHS | Circuit 1 | MCW Shoulder | DI | 25 Sqmm | 1 | 18 | 18 | 35 | 630 | 30 | 660 |  |  | 660
[5 empty] | Circuit 2 | MCW Shoulder | DI | 25 Sqmm | 19 | 33 | 15 | 35 | 525 | 30 | 555 |  | 535
[6 empty] | MCW Shoulder | DA | 16 Sqmm | 34 | 38 | 5 | 35 | 175 | 0 | 175 |  |  | 175
[6 empty] | Service Road | SA | 16 Sqmm | 1 | 4 | 4 | 35 | 140 | 0 | 140 | 125
[5 empty] | Circuit 3 | Service Road | SA | 6 Sqmm | 1 | 8 | 8 | 35 | 280 | 0 | 280 | 255
36 | 213170 | 214520 | 213+700 Btwn 17 &18 | RHS | Circuit 1 | MCW Shoulder | DI | 25 Sqmm | 1 | 18 | 18 | 35 | 630 | 30 | 660 |  |  | 660
[5 empty] | Circuit 2 | MCW Shoulder | DI | 25 Sqmm | 19 | 33 | 15 | 35 | 525 | 30 | 555 |  | 535
[6 empty] | MCW Shoulder | DA | 16 Sqmm | 34 | 38 | 5 | 35 | 175 | 0 | 175 |  |  | 175
[6 empty] | Service Road | SA | 16 Sqmm | 1 | 4 | 4 | 35 | 140 | 0 | 140 | 130
[5 empty] | Circuit 3 | Service Road | SA | 6 Sqmm | 1 | 8 | 8 | 35 | 280 | 0 | 280 | 255
37 | 215860 | 216910 | 216+420 Btwn 15 & 16 | LHS | Circuit 1 | MCW Shoulder | DI | 35 Sqmm | 1 | 14 | 14 | 35 | 490 | 85 | 575 |  | 545
[6 empty] | Median | DA | 16 Sqmm | 1 | 4 | 4 | 35 | 140 | 15 | 155 |  | 135
[6 empty] | Bus Bay | SA | 16 Sqmm | 1 | 6 | 6 | 35 | 210 | 265 | 475 | 445
[5 empty] | Circuit 2 | MCW Shoulder | DI | 16 Sqmm | 15 | 25 | 11 | 35 | 385 | 160 | 545 |  | 525
38 | 215860 | 216910 | 216+420 Btwn 15 & 16 | RHS | Circuit 1 | MCW Shoulder | DI | 25 Sqmm | 1 | 15 | 15 | 35 | 525 | 65 | 590 |  | 560
[6 empty] | Bus Bay | SA | 16 Sqmm | 1 | 6 | 6 | 35 | 210 | 420 | 630 | 600
[5 empty] | Circuit 2 | MCW Shoulder | DI | 10 Sqmm | 16 | 25 | 10 | 35 | 350 | 135 | 485 |  | 480
39 | 218330 | 218920 | 218+600 Btwn 9 & 10 | LHS | Circuit 1 | Service Road | SA | 6 Sqmm | 1 | 4 | 4 | 35 | 140 | 0 | 140 |  |  | 145
[6 empty] | MCW Shoulder | DI | 6 Sqmm | 1 | 5 | 5 | 35 | 175 | 0 | 175 | 150
|  |  |  | LHS | Circuit 2 | MCW Shoulder | DI | 6 Sqmm | 6 | 11 | 6 | 35 | 210 | 0 | 210 | 200
[6 empty] | Service Road | SA | 6 Sqmm | 5 | 8 | 4 | 35 | 140 | 35 | 175 | 160
|  |  |  | RHS | Circuit 3 | Service Road | SA | 6 Sqmm | 1 | 4 | 4 | 35 | 140 | 0 | 140 | 160
[6 empty] | MCW Shoulder | DI | 6 Sqmm | 1 | 5 | 5 | 35 | 175 | 50 | 225 |  |  | 205
|  |  |  | RHS | Circuit 4 | MCW Shoulder | DI | 6 Sqmm | 6 | 11 | 6 | 35 | 210 | 40 | 250 | 240
[6 empty] | Service Road | SA | 6 Sqmm | 5 | 8 | 4 | 35 | 140 | 40 | 180 | 185
40 | 207730 | 208400 | New Feedar and proposed for both Bus Bay and Truck Lay Bye at 207+600 near RHS Bus Bay | LHS | Circuit 1 | MCW Shoulder | DA | 10 Sqmm | 1 | 5 | 5 | 35 | 175 | 120 | 295 |  |  | 295
[6 empty] | Service Road | SA | 6 Sqmm | 4 | 6 | 3 | 35 | 105 | 40 | 145 | 125
[6 empty] | Service Road | SA | 6 Sqmm | 4 | 6 | 3 | 35 | 105 | 40 | 145 | 125
|  |  |  | RHS | Circuit 2 | Bus Bay | SA | 16 Sqmm | 1 | 6 | 6 | 35 | 210 | 100 | 310 | 270
[6 empty] | MCW Shoulder | DA | 10 Sqmm | 1 | 5 | 5 | 35 | 175 | 120 | 295 |  |  | 295
[6 empty] | Service Road | SA | 6 Sqmm | 4 | 6 | 3 | 35 | 105 | 40 | 145 | 125
[6 empty] | Service Road | SA | 6 Sqmm | 4 | 6 | 3 | 35 | 105 | 40 | 145 | 125
41 | 184+540 | 184+760 | New Feeder at Bus Bays | LHS | Circuit 1 | Bus Bay | SA | 6 Sqmm | 1 | 6 | 6 | 35 | 210 | 180 | 390 | 340
|  |  |  | RHS | Circuit 2 | Bus Bay | SA | 6 Sqmm | 1 | 6 | 6 | 35 | 210 | 165 | 375 | 320
42 | 191+150 | 191500 | New Feeder at Bus Bays | LHS | Circuit 1 | Bus Bay | SA | 6 Sqmm | 1 | 6 | 6 | 35 | 210 | 180 | 390 | 320
|  |  |  | RHS | Circuit 2 | Bus Bay | SA | 6 Sqmm | 1 | 6 | 6 | 35 | 210 | 140 | 350 | 320
43 | 214+800 | 215+100 | New Feeder at Bus Bays | RHS | Circuit 1 | Bus Bay | SA | 6 Sqmm | 1 | 6 | 6 | 35 | 210 | 180 | 390 | 380
|  |  |  | LHS | Circuit 2 | Bus Bay | SA | 6 Sqmm | 1 | 6 | 6 | 35 | 210 | 220 | 430 | 320
[15 empty] | 63031 | 19340 | 24125 | 14990
Cable Mtrs
[6 empty] | UG Cable Size |  | Total |  |  | BOQ |  | Diff
[6 empty] | 6 Sqmm |  | 11240 |  |  | 11420 |  | 180
[6 empty] | 10 Sqmm |  | 11524 |  |  | 11525 |  | 1
[6 empty] | 16 Sqmm |  | 13325 |  |  | 13310 |  | -15
[6 empty] | 25 Sqmm |  | 15206 |  |  | 15305 |  | 99
[6 empty] | 35 Sqmm |  | 9546 |  |  | 9635 |  | 89
[6 empty] | 50 Sqmm |  | 2190 |  |  | 2190 |  | 0
63031

## Resusable UG Cable Qty
Re-Usuable Qty of Exisiting UG Cable - HPSV Lights
S.No | Chainage |  | Side | Cable Size | Removal Qty
| From | To
1 | 172+430 | 173960 | RHS | 25 Sqmm | 30
|  |  |  | 16 Sqmm | 60
|  |  |  | 10 Sqmm | 30
|  |  |  | 6 Sqmm | 90
2 | 172+430 | 173960 | LHS | 25 Sqmm | -
|  |  |  | 16 Sqmm | 30
|  |  |  | 10 Sqmm | 30
|  |  |  | 6 Sqmm | 60
3 | 174765 | 175930 | RHS | 25 Sqmm | 30
|  |  |  | 16 Sqmm | 35
|  |  |  | 10 Sqmm | 30
|  |  |  | 6 Sqmm | 70
4 | 174765 | 175930 | LHS | 25 Sqmm | 30
|  |  |  | 16 Sqmm | 35
|  |  |  | 10 Sqmm | 30
|  |  |  | 6 Sqmm | 65
5 | 177110 | 178630 | LHS | 25 Sqmm | -
|  |  |  | 16 Sqmm | 30
|  |  |  | 10 Sqmm | 90
|  |  |  | 6 Sqmm | 90
6 | 177110 | 178630 | RHS | 25 Sqmm | -
|  |  |  | 16 Sqmm | 140
|  |  |  | 10 Sqmm | 35
|  |  |  | 6 Sqmm | 90
7 | 178630 | 179600 | LHS | 16 Sqmm | 60
|  |  |  | 10 Sqmm | 65
|  |  |  | 6 Sqmm | 85
8 | 178630 | 179600 | RHS | 10 Sqmm | 65
|  |  |  | 6 Sqmm | 75
9 | 179600 | 180540 | RHS | 16 Sqmm | 65
|  |  |  | 10 Sqmm | 35
|  |  |  | 6 Sqmm | 35
10 | 179600 | 180540 | LHS | 16 Sqmm | 30
|  |  |  | 10 Sqmm | 45
|  |  |  | 6 Sqmm | 90
11 | 181950 | 182840 | LHS | 16 Sqmm | 55
|  |  |  | 10 Sqmm | 45
|  |  |  | 6 Sqmm | 90
12 | 181950 | 182840 | RHS | 16 Sqmm | -
|  |  |  | 10 Sqmm | 45
|  |  |  | 6 Sqmm | 95
13 | 182840 | 184100 | LHS | 16 Sqmm | 35
|  |  |  | 10 Sqmm | 35
|  |  |  | 6 Sqmm | 65
14 | 182840 | 184100 | RHS | 16 Sqmm | 70
|  |  |  | 10 Sqmm | 70
|  |  |  | 6 Sqmm | 90
15 | 191971 | 192890 | LHS | 16 Sqmm | 65
|  |  |  | 10 Sqmm | 35
|  |  |  | 6 Sqmm | 60
16 | 192890 | 193580 | LHS | 16 Sqmm | 90
|  |  |  | 10 Sqmm | 90
|  |  |  | 6 Sqmm | 75
17 | 192890 | 193580 | RHS | 10 Sqmm | 95
|  |  |  | 6 Sqmm | 90
18 | 194150 | 194950 | LHS | 25 Sqmm | -
|  |  |  | 16 Sqmm | 35
|  |  |  | 10 Sqmm | 75
|  |  |  | 6 Sqmm | 75
19 | 194950 | 195790 | LHS | 16 Sqmm | 45
|  |  |  | 10 Sqmm | 65
|  |  |  | 6 Sqmm | 90
20 | 194150 | 194770 | RHS | 16 Sqmm | 70
|  |  |  | 6 Sqmm | 90
21 | 194770 | 195790 | RHS | 16 Sqmm | 70
|  |  |  | 10 Sqmm | 70
22 | 196145 | 197740 | LHS | 25 Sqmm | -
|  |  |  | 16 Sqmm | 35
|  |  |  | 10 Sqmm | 75
|  |  |  | 6 sqmm | 75
23 | 196145 | 197740 | RHS | 16 Sqmm | 70
|  |  |  | 10 Sqmm | 70
|  |  |  | 6 Sqmm | 65
24 | 199710 | 200895 | LHS | 16 Sqmm | 60
|  |  |  | 10 Sqmm | 65
|  |  |  | 6 Sqmm | 90
25 | 199710 | 200895 | RHS | 16 Sqmm | 70
|  |  |  | 10 Sqmm | 70
|  |  |  | 6 Sqmm | 70
26 | Truck lay bye | Bus Bay | LHS | 16 sqmm | -
|  |  |  | 10 Sqmm | -
|  |  |  | 6 Sqmm | -
| Truck lay bye | Bus Bay | RHS | 10 Sqmm | -
|  |  |  | 6 Sqmm | -
27 | 201654 | 202490 | LHS | 16 Sqmm | 35
|  |  |  | 10 Sqmm | 65
|  |  |  | 6 Sqmm | 90
28 | 201654 | 202490 | RHS | 10 Sqmm | 65
|  |  |  | 6 Sqmm | 75
29 | 205980 | 206420 | LHS | 16 Sqmm | -
|  |  |  | 10 Sqmm | -
|  |  |  | 6 Sqmm | -
30 | 209300 | 210790 | LHS | 16 Sqmm | 65
|  |  |  | 10 Sqmm | 70
|  |  |  | 6 Sqmm | 70
31 | 209300 | 210790 | RHS | 16 Sqmm | 70
|  |  |  | 10 Sqmm | 90
|  |  |  | 6 Sqmm | 95
32 | 211200 | 212400 | LHS | 16 Sqmm | 35
|  |  |  | 6 Sqmm | 60
33 | 211200 | 212400 | RHS | 10 Sqmm | 75
|  |  |  | 6 Sqmm | 80
34 | 212400 | 213160 | LHS | 10 Sqmm | 40
|  |  | RHS | 6 Sqmm | 90
35 | 213170 | 214520 | LHS | 16 Sqmm | 40
|  |  |  | 10 Sqmm | 40
|  |  |  | 6 Sqmm | 65
36 | 213170 | 214520 | RHS | 16 Sqmm | 70
|  |  |  | 10 Sqmm | 70
|  |  |  | 6 Sqmm | 85
37 | 215860 | 216910 | LHS | 16 Sqmm | 65
|  |  |  | 10 Sqmm | 75
|  |  |  | 6 Sqmm | 90
38 | 215860 | 216910 | RHS | 10 Sqmm | 65
|  |  |  | 6 Sqmm | 90
39 | 218330 | 218920 | LHS | 6 Sqmm | 60
Total UG Cables to be Resued |  |  |  |  | 6560
|  |  |  | Cable Size | Cable Mtrs
Total
|  |  |  | 25 Sqmm | 90
|  |  |  | 16 sqmm | 1635
|  |  |  | 10 sqmm | 2015
|  |  |  | 6 sqmm | 2820