## BOQ Final
Subject:- BOQ for Electrical improvement works for Highway Street Lights & Toll Plaza submitted by Designtech MEP Consultants.
Sr. No | Specification | UOM | PR.Qty. | Rate | Amount | Remark
1 | MAIN STREET LIGHT FEEDER PILLAR Complete SITC Set of Main Street Feeder Pillar as below Electrolytic grade Aluminium bus bar by means of SMC / DMC type insulator 110/220 V LED (22.5 mm dia ) R Y B ON Indicating lamp with integral circuit terminal block including connection etc. as required. Electrical insulating rubber matts confirming to IS: 15652 / 2006 with one side anti skid aberration marks and pasting the mat with synthetic rubber adhesive as required. 11 KV 2.5 mm thick with proof voltage 22 KV / 3 min. and Break Down Voltage 45 KV Current Transformer with all necessary support in existing panel including connection etc. as required . from 40/5 to 63/5 Ratio 10 VA class 1 accuracy 0.5 A to 4 A rating (Protection MCB) CT operated direct reading type Ampere meter on existing panel making connection by PVC insulated copper conductor with PVC sleeves / channel etc. as required. Below 500 A (Digital type) (0-500) V range Volt meter on existing panel making connection by PVC insulated copper conductor with PVC sleeves / channel etc. as required. Digital type selector switch of 10 A for voltmeter (4 position ) including making connection etc. as required . CT linked selector switch of 10 A for Ampere meter (4 position ) including making connection etc. as required . Totally enclosed Plinth mounted dust vermin proof double door outdoor type IP55 Feeder Pillar made out of min 3mm sheet complete complete including foundation civil and structural works INCOMING P&F 415 V AC FP MCB with positive isolation of breaking capacity not less than 10/16 KA (B/ C/ D tripping characteristic) ISI marked IS 8828(1996)]/ conforming to IEC 60898 in existing board/sheets including making connections with lugs testing etc. as required. 63 Amp 10 kA - 1 nos. OUTGOINGS P&F 240/415 V AC MCB with positive isolation of breaking capacity not less than 10 KA (B/ C/ D tripping characteristic) ISI marked IS 8828(1996)]/ conforming to IEC 60898 in existing board/sheets including making connections with lugs testing etc. as required. Double pole MCB 32 A rating ( 2 no.) Four pole MCB 6 A to 25 A rating ( 8 no.) 1no. 110 - 240 V AC 1 ph. 2 W Astronomical time switch with surge suppressor memory card Sunrise / Sunset selectable software for programming including making connection etc. as required Provide Space for energy meter in panel compartment ( Energy meter will be supplied & Installed by DISCOM ) P & F of ac operated heavy duty 230 /415 Volt power contactor conforming to IS:13947-4-1/IEC:947-4-1 having provision of mechanical interlocking auxilary contacts Din rail mounting type including making connections testing etc. as required. 4 pole Power Contactors with following AC 1 Rating 40-63 Amp. | Nos | 35 |  |  | In Place of Rusted, Damaged or Missing Panel, Location wise sheet is attached for referece
2 | MCB 6A-32A 2 Pole Providing & erecting 240 V MCB double pole switch for lighting Load (B Curve) having 10 KA breaking capacity & confirms to IS : 8828 in existing box having following capacity 6 to 32 Amp | Nos | 100 |  |  | The quantity is considered approximate and will be installed only if required, based on the site conditions at the time of work execution.
3 | MCB 32A 4 Pole Providing & erecting 415V MCB Four Pole Switch for Lighting Load (B curve) having 10KA breaking capacity & confirms to IS :8828 in existing box having following capacity | Nos | 10 |  |  | The quantity is considered approximate and will be installed only if required, based on the site conditions at the time of work execution.
4 | MCB 40A 4 Pole Providing & erecting 415V MCB Four Pole Switch for Lighting Load (B curve) having 10KA breaking capacity & confirms to IS :8828 in existing box having following capacity | Nos | 10 |  |  | The quantity is considered approximate and will be installed only if required, based on the site conditions at the time of work execution.
5 | MCB 63A 4 Pole Providing & erecting 415V MCB Four Pole Switch for Lighting Load (B curve) having 10KA breaking capacity & confirms to IS :8828 in existing box having given capacity | Nos | 60 |  |  | The quantity is considered approximate and will be installed only if required, based on the site conditions at the time of work execution.
6 | MCB 6A-25A 1 Pole providing and erecting Miniature circuit breaker single pole 6A to 25A suitable to operate on 240 V A.C. system and having breaking capacity 10 KA to be erected in existing box. confirming to IS 8828/1996 with ISI Mark | Nos | 1000 |  |  | Major requirement of 1 Pole MCB required for all existing 699 No's LED light fixture (263.000, 290.600, 306.100, 314.640, 348.600, 370.700, 382.750, 403.400, 403.650, 413.850, 416.750) othar all location (Ch:-270-419) where HPSV Light fixture available in Place of Damaged/Missing MCB
7 | Contactor 4 pole 440V 63 Amp Make L&T Supplying & erecting power contactor AC3 duty for time switch complete erected as per direction Cat III | Nos | 60 |  |  | The quantity is considered approximate and will be installed only if required, based on the site conditions at the time of work execution.
8 | 16 Sq.mm ( 4 core) XLPE Aluminium Armoured Cable Make Polycab KEI RR Cable Proving & Laying XLPE insulated & P.V.C. sheathed cable of 1.1 KV grade with aluminium conductor of IS:1554 P-I / IS :7098 P - I in ground or laying HDPE / DWC pipe. Rate also includes Supplying and making one end termination with heavy duty single compression brass gland SIBG type heavy duty aluminium lugs duly crimped with crimping tool PVC tape etc for following size of Armoured PVC sheathed / XLPE aluminium conductor cable of 1100 volt grade, for TMS, & Street Light at Site & Toll Plaza. | Rmt | 25000 |  |  | The existing overhead cable installed along the roadside for street lighting is required to be replaced with a suitably rated underground cable. The current underground/overhead unarmoured cable laid at the crash barrier is of low quality and has inadequate load-carrying capacity, resulting in repeated major faults, overheating, and short-circuiting of the pole-to-pole cable. Replacing it with a properly rated underground cable will improve system reliability, prevent recurring failures, and ensure safe and efficient operation of the street lighting network.
9 | 25 Sq.mm (4 core) XLPE Aluminium Armoured Cable Make- Polycab KEI RR Cable Proving & Laying XLPE insulated & P.V.C. sheathed cable of 1.1 KV grade with aluminium conductor of IS:1554 P-I / IS :7098 P - I in ground or laying HDPE / DWC pipe. Rate also includes Supplying and making one end termination with heavy duty single compression brass gland SIBG type heavy duty aluminium lugs duly crimped with crimping tool PVC tape etc for following size of Armoured PVC sheathed / XLPE aluminium conductor cable of 1100 volt grade for highway Street Light at Site & Toll Plaza cable renovation. | Rmt | 20000 |  |  | Cable is required at the toll plaza for renovation works and for the replacement of damaged cables used for street lights and high-mast lighting. The replacement cable shall be selected as per the connected electrical load and prevailing site conditions to ensure safe, reliable, and efficient operation of the lighting system. Backup sheet is attached for reference
10 | 35 Sq.mm (4 core) XLPE Aluminium Armoured Cable Make- Polycab KEI RR Cable Proving & Laying XLPE insulated & P.V.C. sheathed cable of 1.1 KV grade with aluminium conductor of IS:1554 P-I / IS :7098 P - I in ground or laying HDPE / DWC pipe. Rate also includes Supplying and making one end termination with heavy duty single compression brass gland SIBG type heavy duty aluminium lugs duly crimped with crimping tool PVC tape etc for following size of Armoured PVC sheathed / XLPE aluminium conductor cable of 1100 volt grade for highway Street Light at Site & Toll Plaza cable renovation. | Rmt | 2000 |  |  | Cable is required at the toll plaza for renovation works and for the replacement of damaged service cables from the transformer to the energy meter and from the energy meter to the feeder pillar, serving the street lighting and high-mast lighting systems.
11 | 50 Sq.mm (3.5 core) XLPE Aluminium Armoured Cable Make- Polycab KEI RR Cable Proving & Laying XLPE insulated & P.V.C. sheathed cable of 1.1 KV grade with aluminium conductor of IS:1554 P-I / IS :7098 P - I in ground or laying HDPE / DWC pipe. Rate also includes Supplying and making one end termination with heavy duty single compression brass gland SIBG type heavy duty aluminium lugs duly crimped with crimping tool PVC tape etc for following size of Armoured PVC sheathed / XLPE aluminium conductor cable of 1100 volt grade for highway Street Light at Site & Toll Plaza cable renovation. | Rmt | 1000 |  |  | Cable is required at the toll plaza for renovation works and for the replacement of damaged service cables from the transformer to the energy meter and from the energy meter to the feeder pillar, serving the street lighting and high-mast lighting systems.
12 | 70 Sq.mm (3.5 core) XLPE Aluminium Armoured Cable Make- Polycab KEI RR Cable Proving & Laying XLPE insulated & P.V.C. sheathed cable of 1.1 KV grade with aluminium conductor of IS:1554 P-I / IS :7098 P - I in ground or laying HDPE / DWC pipe. Rate also includes Supplying and making one end termination with heavy duty single compression brass gland SIBG type heavy duty aluminium lugs duly crimped with crimping tool PVC tape etc for following size of Armoured PVC sheathed / XLPE aluminium conductor cable of 1100 volt grade, for highway Street Light at Site & Toll Plaza cable renovation. | Rmt | 1000 |  |  | Cable is required at the toll plaza for renovation works and for the replacement of damaged service cables from the transformer to the energy meter and from the energy meter to the feeder pillar, serving the street lighting and high-mast lighting systems.
13 | DWC HDPE PIPE 63 mm dia (OD-63 mm & ID-51 mm nominal) Supplying and laying of following size DWC HDPE pipe ISI marked along with all accessories like socket bend couplers etc. conforming to IS 14930 Part II complete with fitting and cutting jointing etc.direct in ground (75 cm below ground level) including excavation and refilling the trench including sand cushioning complete as required or Directly install on behind the Crash barrier of VUP / PUP / Flyover / ROB / etc. with complete accossories SS saddles nuts bolts complete as required for Cable laying pipe from pole to pole. Replace as when required, for ATMS & highway Street Light at Site & Toll Plaza cable for cable renovation. | Rmt | 10000 |  |  | DWC HDPE pipe is required at the toll plaza for renovation works, for Laying of ATMS supply at site and for the replacement of damaged undergrund cables from Pole to Pole. Location wise sheet is attached for referece
14 | DWC HDPE PIPE 100 mm Dia (OD-100 mm & ID-90 mm nominal) Supplying and laying of following size HDPE pipe ISI marked along with all accessories like socket bend couplers etc. conforming to IS 14930 Part II complete with fitting and cutting jointing etc.direct in ground (75 cm below ground level) including excavation and refilling the trench including sand cushioning complete as required or Directly install on behind the Crash barrier of VUP / PUP / Flyover / ROB / etc. with complete accossories SS saddles nuts bolts complete as required Replace as when required, | Rmt | 1500 |  |  | Laying of DWC HDPE pipe is required at the toll plaza for renovation works it will be laying throgh the chamaber to chamber., Location wise sheet is attached for referece
15 | HDD Work With 100 mm Dia PN6-8 grade HDPE Pipe Providing and laying / Insert HDPE pipe for HT / LT underground cable including laying jointing insertation of hdpe pipe 2 nos x 100mm dia and 6 mm thickness without damaging surface / Road by using horizontal auger guided boring / Horizontal directional drilling machine by push and loop method. Insert of hdpe pipe in side Road boundary by cut and fill method. Rate are included with Providing and supply of hdpe pipe - 2 nos x 100mm dia. | RMT | 1500 |  |  | Laying of DWC HDPE pipe is required at the toll plaza for renovation works it will be laying . Location wise sheet is attached for referece
16 | HDD Work With 100 mm or 63 mm Dia PN6-8 grade HDPE Pipe Providing and laying / Insert HDPE pipe for HT / LT underground cable including laying jointing insertation of hdpe pipe 1 Nos x 100 mm dia or 1 nos x 63mm dia and 6 mm thickness without damaging surface / Road by using horizontal auger guided boring / Horizontal diractional drilling machine by push and loop method.Insert of hdpe pipe in side Road boundary by cut and fill method. Rate are included with Providing and supply of hdpe pipe - 1 nos x 63mm dia. | RMT | 1000 |  |  | Laying of DWC HDPE pipe is required at the toll plaza for renovation works it will be laying . Location wise sheet is attached for referece
17 | Birck Wall Electrical Chamber with Cover Constructing brick masonry manhole / Chamber in cement mortar 1:4 ( 1 cement : 4 coarse sand ) with R.C.C. top slab with 1:1.5:3 mix (1 cement : 1.5 coarse sand (zone-III) : 3 graded stone aggregate 20 mm nominal size) foundation concrete 1:4:8 mix (1 cement : 4 coarse sand (zone-III) : 8 graded stone aggregate 40 mm nominal size) inside plastering 12 mm thick with cement mortar 1:3 (1 cement : 3 coarse sand) finished with floating coat of neat cement and making channels in cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) finished with a floating coat of neat cement complete as per standard design : Inside size 1200x900 mm and 900 mm deep including C.I. cover with frame (medium duty) 500 mm internal diameter total weight of cover and frame to be not less than 116 kg (weight of cover 58 kg and weight of frame 58 kg) : | Nos | 32 |  |  | at the toll plaza for cable renovation works , the cable will be laying throgh the chamaber to chamber., Location wise sheet is attached for referece
18 | GI Chemical Earthing Providing Fixing & Testing of Maintenance free Gel Earthing with Pipe in Strip Technology filled with anti-corrosive conductive compound (CPRI Tested) below the ground in 150 - 200 mm dia. earth pit & surrounding filled with required mineral filling compound (MFC should have hygroscopic property to retain the moisture for long time to create low resistance zone) and C.C. finished chamber covered with hinged type with locking arrangement C.I. Cover C.I. Frame of size 300mm x 300mm complete testing of earth resistance as required. of following sizes. With Pipe in Strip Technology (Inner pipe dia. / Outer pipe dia. ) 80 - 100-micron GI Coating.GI Pipe 2000 mm Long 50 / 25mm Terminal 12 mm GI Strip. For highway street Light High mast Pole & Panel earthing as per site requirement | Nos | 400 |  |  | For Street Light pole & Panel, highmast Pole & Panel body earthing at site
19 | Copper Chemical electrode 50X3000 MM Earthing Work for Neutral & Body earthing of essential Electrical Equipment (Transformer VCB Cubical energy Meter DG & etc at Toll Plaza. SITC of Maintenance Free Copper Chemical electrode (99.9 % Pure) as per standard IS 3043:1987 inclusive of Manpower Material Machinery with the following specifications: (a) Copper Chemical electrode 50X3000 MM. (b) GI Mess Pipe 40X2000 mm (c) Copper Strip: 25X3 MM from earthing electrode to nearest Electrical Equipment. (d) Bentonite Powder /Charcole & Salt mixture 25 kg for every earthing pit/ As needed. (e) Heavy Duty Earthing Chamber (HDPE Square Type) Earthing Chamber having dimensions 300mmX300X260mm with concereting of Chamber for every earth Pit. (f) The Value of each earthing should be less than 3 Ohm. It will be the responsibility of contactor/ agency to pour appropriate quantity of water in all the earthing during the work of each earthing. | Nos | 16 |  |  | Provision for body earthing and neutral earthing shall be made for essential electrical equipment. The location-wise earthing details sheet is enclosed herewith for reference.
20 | GI Chemical electrode 50X3000 MM Earthing work for Body earthing of Electrical Equipment at Toll Plaza SITC of Maintenance Free GI Chemical electrode as per standard IS 3043:1987 inclusive of Manpower Material Machinery with the following specifications: (a) GI Chemical electrode 50X3000 MM. (b) GI Mess Pipe 40X2000 mm. (c) GI Strip: 25X3 mm from earthing electrode to nearest Electrical Equipment. (d) Bentonite Powder /Charcoal & Salt mixture 25 kg for every earthing pit / As needed. (e) Heavy Duty Earthing Chamber (HDPE Square Type) Earthing Chamber having dimensions 300mmX300X260mm with concreting of Chamber for every earth Pit. (f) The Value of each earthing should be less than 3 Ohm. (g) It will be the responsibility of contactor/ agency to pour appropriate quantity of water in all the earthing during the work of each earthing. | Nos | 56 |  |  | For electrical equipment body earthing Location wise sheet is attached for referece
21 | Vertical Air Termination / Lightning Arrester for electrical Building SITC of Vertical Air Termination Solid aluminium with Base- 10 mm dia and 1000 mm long. Air Termination Base tested for conditioning; Ageing Test & Lightning impulse current withstand test: 100 kA of 10/350µs waveform in an accredited Third party laboratory as per 6.3 & 6.4 of IEC 62561-1 2017 protocol with MAST 34mm dia Cold Galvanized. complete with all mounting post clamps nuts bolts insulators etc. | Nos | 2 |  |  | For Both Toll Electrical Building
22 | GI Earthing Strips Supply & Laying Hot Deep required size GI earth strip in horizontal or vertical run in ground/surface/recess including riveting soldering saddles making connection etc. as required. | NOS | 1800 |  |  | For electrical equipment body earthing Location wise sheet is attached for referece
23 | Copper Earthing Strips Supply & Laying required size Copper strip in horizontal or vertical run in ground/surface/recess including riveting soldering saddles making connection etc. as required. | NOS | 150 |  |  | Provision for body earthing and neutral earthing shall be made for essential electrical equipment. The location-wise earthing details sheet is enclosed herewith for reference.
24 | Copper Flexi cable 70 sq. mm Supply & fixing of 70 sq.mm PVC insulated Copper flexible cable as down conductor complete install with saddles/clamps. | Rmt | 150 |  |  | For Both Toll Plaza LA earthing for Electrical Building
25 | Lightning Strike Counter SITC of Lighting counter - To count no of lightning strike & it can record the date and time of the lightning having plastic encloser IP-65. Measuring Range: 0-100 KA Display: LCD-with 0-999 count operating temprature: -20 to 60 degree celcius No odsensor:1 nos (JEF CAPE DEHN OBO Better Man make) | Nos | 2 |  |  | For Both Toll Plaza LA earthing for Electrical Building
26 | 10 Mtr. GI Octagonal Street Light Pole Supply installation testing & commissioning of 10 mtr Supply and installation (Excluding foundation work) of 10 m ( clear pole height is 10 mtr. from road surface On main carriage Way. Long 70 mm Top X 175mm bottom dia 3 mm thickness Octagonal poles. Made from CR sheet steel. The pole should be made as per IS. and shall be coated with hot dip galvanizing as per IS 2629/4759. with required base plate suitable suspend local wind speed ( 140 km/Hr) and pole base is heavy MS plate welded with pole bottom with M 24 x 750 long ’J’ type EN 8 grade foundation bolts along with template for the above poles.with Rate includes (a) Supply & erection of Bakelite sheet with 2 no. 6A SP MCB & External surge protector - 20 kV & stud type terminal block suitable upto 4Cx35 sq. mm Cable. (b) Supply & Installation of 3Cx1.5 sq. Cu Flexible FRLS Wire for connection of light fitting.( From Pole JB to light fixtures ) (C) Spiral Earthing ( If ground Available ) for each streetlight pole complete with 8 SWG galvanized wire having 5 feet deep in ground and 1 feet spiral portion covered by salt coal etc. or Connect earthing through cable steel / wire armoured only. (D) For Earthing if ground is not available In that case Pole earthing on flyover / ROB / VUP / PUP etc will be by laying 8 SWG GALVANISED wire along with pole to pole cables from feeder pillars. | Nos | 100 |  |  | For Damaged street Light pole repacement , details sheet is enclosed herewith for reference.
27 | Copper Flexi Cable 3X1.5 Sq. mm Supply & Installation of 3Cx1.5 sq. Cu Flexible FRLS Wire for connection of light fitting. ( From Pole Junction Box to light fixtures) | Rmt | 12000 |  |  | ( From Pole Junction Box to light fixtures), details sheet is enclosed herewith for reference.
28 | Single Arm 1.0 Mtr 10 Degree Supply Installation Testing & Commissioning of 1.0 mtr. long & 10-degree Tilt angle Hot dip galvanised Single Arm bracket made up of 40NB dia GI pipe suitable to mount on TOP of pole having top 70mm A/F or as per existing pole top pipe diameter. | Nos | 20 |  |  | For Damaged street Light pole repacement , details sheet is enclosed herewith for reference.
29 | Double Arm 2 Mtr. 16 Degree Supply Installation Testing & Commissioning of 2 mtr long & 16-degree Tilt angle hot dip galvanised Single Arm bracket made up of 40NB Dia GI pipe suitable to mount on Side of pole on Service Roadside (Differential Arm pole) | Nos | 30 |  |  | For Damaged street Light pole repacement , details sheet is enclosed herewith for reference.
30 | Double Arm 2.5 mtr 10 Degree Supply Installation Testing & Commissioning of 2.5 mtr. Long & 10 degree Tilt Angle hot dip galvanised Double Arm bracket made up of 40NB dia GI pipe suitable to mount on TOP of pole having top 70mm A/F or as per existing pole top pipe diameter. | Nos | 50 |  |  | For Damaged street Light pole repacement , details sheet is enclosed herewith for reference.
31 | RCC Foundation (M20) for 10 Mtr Octagonal Pole RCC Foundation (M20) for 10 Mtr Octagonal Pole Providing of RCC Foundation (M20) Foundation Size: 600mm x 600mm x 1200 mm. with bolts 4 nos of octagonal pole including excavation of pole pit. The scope shall also include grouting of foundation bolts including watering and ramming & provision for passage of cable by using suitable size GI pipe / DWC pipe / HDPE pipe. Vendor submit the civil foundation details from structure consultants for approval from IE / Client Note:- If the any existing foundation is found suitable for installation of the new pole the same will be used after approval and construction of new foundation will not be required. | Nos | 100 |  |  | For Damaged street Light pole repacement , details sheet is enclosed herewith for reference.
32 | L Bracket with Fastener/ Bolt for 10 mtr Octagonal Street Light Pole SITC of MS wall mounted steel bracket on RE wall to rest streetlight octagonal pole incl. Hilti make fastener. Contractor shall have to submit structural design for the same. Vendor submit the MS Foundation bracket details from structure consultants for approval from IE / Client | Nos | 20 |  |  | Some poles at Km 295 and Km 403 are hanging due to improper fixing and require re-fixing to ensure proper alignment and structural stability.
33 | 200W LED STREET LIGHT FOR MAIN CARRIAGEWAY LIGHTING + SERVICE ROAD LIGHTING SITC of 200W SMD LED Streetlight fixture with System efficacy of 135 lm/W (27000 lumens). Luminaire shall be made up of pure polyester powder coated die cast Aluminium housing with IP rated high purity Polycarbonate lens . The luminaire should have a dimension of 417mm x 285mm x 2mm ± 2mm appoximate weight of 3.8 Kg ± 0.25 Kg. The housing should be made of LM6/ADC12 Alloy non-corrosive Single Piece pressure die-cast aluminum to withstand extreme environments. All external hardware must be of SS304 grade. Luminaire shall be designed with street optic LENS for uniform light distribution. Maximum LENS dome top temperature shall be less than 95°C at 45°C ambient temperature. LM 80-08 compliant LEDs of EMC/ceramic package of wattage of 4W-5W from reputed makes such as Nichia/Cree/ Bridgelux/ Lumiled/ Osram/Seoul should be provided. LEDs used in the product shall comply with EN 62471 for Photo-biological safety and certificate for the same from manufacturer shall be provided. Luminaire shall be with IP66 and IK10 protection. The LED shall be compliant with LM80-08 standard with L70 life of 50000 Hrs tested at maximum current (Complete LM 80 test report for LED should be submitted for 10000 hrs of testing). The LEDs used should be with CCT of 5700 K CRI of Minimum 70 and SDCM of < 5. LEDs must be driven at max 70% of the rated current. MCPCB with Aluminium core and copper thickeness of 35 micron to be used for LED mounting. LED Driver shall be silicone potted Integrated type Isolated Constant Current with range 140-280V AC. Driver Efficiency > 88% & 4 KV internal surge protection with additional 10KV SPD mounted inside the luminaire and firmly fixed to the housing Power factor greater than 0.95 and total harmonic distortion (THD) of less than 10% should be integral to the luminaire. LED Driver must have short circuit open circuit Auto cut-off protection for low and high input voltage. Driver must have 440V input voltage protection for 8 hours. LED driver should have over temperature protection. Manufacturer shall have inhouse lab approved by NABL or ministry of science of govt of India. LM 79 and LM80 reports need to be submitted from a NABL/UL accredited lab to verify above parameters. Compliance to Indian Standards of IS10322 Part 5 / Sect 3:2013; 16105 : 2012; IS 16106 : 2012; IS 15885 (Part2/Sec13) : 2012; IS 16108 : 2012. Make-Wipro/Philips/Bajaj/Crompton/Havells Safely removing and shifting old fixtures, and depositing them in writing at the toll plaza or store, etc. | Nos | 2550 |  |  | Required Total installation of 200 W LED Light fixture in place of 400W HPSV , details sheet is enclosed herewith for reference.
34 | Wallmounted 80 W LED Flood Street Light FOR UNDERNEATH VUP LIGHTING SITC of 80 W LED High bay light having min system lumen output of 10500. Min system Efficacy should be > 130 Lm/w. Housing Should be made up of Al die cast having High Transmittance Polycarbonate cover. Luminaire should be IP66 and IK08 Protected. Luminaire should have proper Heat sink for thermal management with eye bolt mounting. Luminaire should have beam angle of 110 Deg Wide beams for proper light distribution CRI > 80 SDCM < 5 with lifeclass of 50000 Hrs @L70B50.. Driver use should be of potted and encapsulated only. Operating voltage range of driver should be of 140 – 270 VAC with 4 KV internal surge protection THD < 10% PF > 0.95 High voltage cut off & Auto restart @ 320 VAC Phase to phase 440 V Protection for 8 Hrs. Driver should be of reputed makes such as Philips Xitanium / Osram / Meanwell only. Driver & luminaire both should be BIS Approved only. Luminaire should be tested under NABL Accredited Lab for LM79/LM80/TTC. Similar to Philips BY225P LED100S CW WB PSU FG GR | Nos | 210 |  |  | Location for underpass lighting details sheet is enclosed herewith for reference.
35 | Highmast Repairing Supply & Laying of raising lowering system comprising double drum winch 6 / 8 mm diameter SS wire rope trailing cable connector integral power tool motor manual handle junction box lightening finial. | Nos | 30 |  |  | The quantity is considered approximate and will be done only if required, based on the site conditions at the time of work execution.
36 | Aviation lamp for High mast SITC of LED type double dome aviation obstruction light for 30 Mtr Highmast. | Nos | 30 |  |  | The quantity is considered approximate and will be done only if required, based on the site conditions at the time of work execution.
37 | Re-installation of High mast pole when required Erection of the high mast with the help of suitable tools and plants wiring of luminaries with all wiring materials like PVC insulated PVC sheathed flexible cable of suitable copper conductor cores of 1.5 sq. mm lugs MCB and all labour as a complete job. Rate include cranes for using lowering & re-installation of High mast pole. | Nos | 10 |  |  | The quantity is considered approximate and will be done only if required, based on the site conditions at the time of work execution.
38 | HIGH MAST FEEDER PANEL 30 Mtr Highmast SITC of outdoor stand mounted feeder pillar with 40A TPN MCB incomer single dial time switch 40A FP contactor for the automatic switching of luminaries power tool control with 2 no 9A contactors and raise lower push button Incoming 35 sq. mm and out going 20 x1.5 sq. mm terminals. (4) Construction of shallow foundation with M20 grade concrete for the highmast considering the safe soil bearing capacity at site as 10 T/sqmtr at 2 metre depth with all materials and labour. (Foundation civil design will be approved by structural consultants). | Nos | 35 |  |  | Location for installation of Highmast Control Panel details sheet is enclosed herewith for reference.
39 | 400 WATT LED LIGHTING FIXTURES FOR HIGH MAST @ ALL JUNCTIONS + GRADE SEPARATED JUNCTIONS ETC. SITC of 400W SMD LED Floodlight fixture with System efficacy of 125 lm/W (50000 lumens). Luminaire shall be made up of LM6/ADC12 Alloy non-corrosive pure polyster power coated die cast Aluminium housing with PC lens. Lumianire should be of dimension 319mm x 507mm x 97mm height ± 5mm height and the approximate weight should be within the 12.0Kg ± 0.5Kg. Luminaire should be available with 25° and 60° beam angle option. Luminaire should be made of four individual modules of 100W to 125W each. All external hardware must be of SS304 grade. LM 80-08 compliant LEDs of EMC/ceramic package of wattage of 5W from reputed makes such as Nichia/Cree/ Bridgelux/ Lumiled/ Osram/Seoul should be provided. LEDs used in the product shall comply with EN 62471 for Photo-biological safety and certificate for the same from manufacturer shall be provided. Maximum LENS dome top temperature shall be less than 95°C at 45°C ambient temperature. Luminaire shall be with IP66 and IK07 protection. It should be cabable to operating under ambient temperature range of -10°C to +45°C. The LED shall be compliant with LM80-08 standard with L70 life of 50000 Hrs tested at maximum current (Complete LM 80 test report for LED should be submitted for 10000 hrs of testing). The LEDs used should be with CCT of 5700 K CRI of Minimum 70 and SDCM < 5. LEDs must be driven at max 70% of the rated current. MCPCB with Aluminium core and copper thickeness of 35 micron to be used for LED mounting. LED Driver shall be silicone potted Integrated type Isolated Constant Current with range 140-280V AC. Driver Efficiency > 88% & 4 KV internal surge protection with additional 10KV SPD mounted inside the luminaire and firmly fixed to the housing Power factor greater than 0.95 and total harmonic distortion (THD) of less than 10% should be integral to the luminaire. LED Driver must have short circuit open circuit Auto cut-off protection for low and high input voltage. LED driver should have 440V AC protection for atleast 8 hours.LED driver should have over temperature protection.Individual drivers should be provided with individual modules along with ventilated enclousure to hide the wirings. Driver must be with Aluminium casing. Manufacturer shall have inhouse lab approved by NABL or ministry of science of govt of India. LM 79 and LM80 reports need to be submitted from a NABL/UL accredited lab to verify above parameters. Compliance to Indian Standards of IS10322 Part 5 / Sect 5:1967; 16105 : 2012; IS 16106 : 2012; IS 15885 (Part2/Sec13) : 2012; IS 16108 : 2012. | Nos | 510 |  |  | Location for installation/replacement of Highmast LED Light fixture in Place of HPSV Fixture, details sheet is enclosed herewith for reference.
40 | Internal Electrical Wiring (Lighting Circuit) for Toll Plaza :- Providing and erecting Point wiring with 1.1 KV grade ISI marked 2 X 1.5 sq. mm copper PVC insulted FRLS wire with 1.5 sq. mm (green) copper PVC insulated FRLS wire for earth continuity in FIA approved ISI mark medium class white colour 20/25 mm dia. embossed rigid PVC pipe with PVC fitting fixed with adhesive solution erected on/in Brick Wall / slab along with continuous G.I. fish wire to draw wires and laid in approved manner zari for PVC pipe and boxes shall be filled with cement mortar and finishing the surface to match the wall / ceiling complete with approved make 5/6 Amp. ISI make modular type switch and accessories mounted in 20 G. G.I. company fabricated metallic box covered with appropriate front plate modules erected flushed with wall / ceiling with necessary modular lamp holder / modular ceiling rose / HD Connector (make & model approved by EIC and matching colur with switches accessories) (Deep Junction box 75mm depth if required) as directed for concealed wiring. Light point. Necessary sheet / tape / polythene / sand must be erected or filled in all box to prevent mortar going into the box. Length of point wiring must not increase than 10 mtr. For that necessary switch boards and their locations must be finalised before execution by agency otherwise payment will not be done for extra long point. (For future extention if required agency has to erect one higher size metal box and modular plate as per instruction of EIC. Cost of blank plate shall be paid as per tender item) [This item include cleaning (inside/outside) of all G.I. switch boards electric point box fan box MCBDB & box cutting plaster finishing for modular plate without any gap] [conductor resistance should be as per IS:8130/1984] | NOS | 100 |  |  | The quantity is considered approximate and will be done only if required, based on the site conditions at the time of work execution.
41 | Internal Electrical power Wiring for Toll Plaza :- Providing and fixing Plug Point wiring with 1.1 KV grade ISI marked approved make 2 x 2.5 sq.mm copper PVC insulated FRLS wire with 1.5 sq.mm (green) copper PVC insulated FRLS wire for earth continuity in FIA approved ISI mark white colour medium class 20/25 mm dia. embossed rigid PVC pipe with PVC fitting fixed with adhesive solution erected in wall/slab along with continuous G. I. fish wire to draw wires and laid in approved manner zari for PVC pipe & boxes shall be filled with cement mortar & finishing the surface to match the wall / ceiling complete with 16 Amp Modular type Swich and accessories mounted in 20 G. GI company fabricated metallic box covered with appropriate front plate modules erected flushed with wall. (a) 16 Amp. Indicator switch & 1 No. 6/16 A universal socket white colour suitable for 3/5 pin top duly both having ISI mark. (Necessary sheet / tape / polythene / sand must be erected or filled in all box To Prevent Mortor Going In To The Box) (Conductor resistance should be as per IS:8130/1984) ( FOR POWER PLUG IN BOOTH & ADMIN BUILDING ) | NOS | 40 |  |  | The quantity is considered approximate and will be done only if required, based on the site conditions at the time of work execution.
42 | Power Wiring for (A.C POINT / BLOWER ONLY FOR BOOTH & ADMIN BUILDING) Providing & Erecting Plug Point wiring with approved ISI marked 1.1 kv grade 2 x 4.0 sq.mm copper PVC insulated FRLS wire with 2.5 sq.mm (green) copper PVC insulated FRLS wire for earth continuity in FIA approved ISI mark white colour medium class 25 mm dia. embossed rigid PVC pipe with PVC fitting fixed with adhesive solution erected in wall / slab along with continuous G.I. fish wire to draw wires and laid in approved manner. zari for PVC pipe & boxes shall be filled with cement mortar & finishing the surface to match the wall / ceiling complete with approved make 20 Amp. Modular type indicator switch and accessories mounted in 20 SWG GI company fabricated metallic box covered with appropriate front plate modules erected flushed with wall / ceiling. (a) 20 Amp Indicator switch & 1 No. 20 A universal socket white colour suitable for 3 pin top duly both having ISI mark(A.C POINT / BLOWER ONLY FOR BOOTH & ADMIN BUILDING ) (Necessary sheet / tape / polythene / sand must be erected or filled in all box to Prevent Mortor Going In to The Box) the quantity will be consider in set/point. | NOS | 60 |  |  | The quantity is considered approximate and will be done only if required, based on the site conditions at the time of work execution.
43 | Surge Protection Device (SPD) Supply Installation Testing & Commissioning of Three Phase 440 V Surge Suppressor protection Device (SPD) & 40 Amp TPN MCB (or As per SPD OEM guide line for the protection of SPD which is erected such a way that it can be operated easily) SPD must be capable to protect all electrical and electronics equipments if SPD blast or fuse then the panel builder must have replace it soon during defect liability period. (Hakel ikra OBBO make) (With Three year Gaurantee/warranty) | Nos | 6 |  |  | For Electrical equipment safety, It will be installed in 1 No's in Admin building & 2 No's in SWB Building at both toll plaza
44 | 6-Way SPN DB Board Double Door SITC of Approved make 6-Way SPN Double Door metal clad D.B. company prewired having Incoming and outgoing as mentioned below with NL suitable to operate on 230 Volt A.C. power and having overload and short circuit tripping element breaking capacity 10KA (for all MCB & ELCB) to be erected in flush type and company fabricated 16 G.M.S./ IK 08 Certificate sheet box with powder coated inside and outside after apply seven tank chemical process of M.S. sheet cover complete with suitable integral single piece construction tinned copper busbar- and link with all necessary interconnection and with neccessary size wooden board for mounting MCBDB . Manufacturer must be Provided .(1)IP 43 Protection Certificate.(2) Seven tank Powder Coating Certificate.(3) Copper/Brass make Neutral & Earthing link with Isolation and Protecting Cover. (a) For 6 Way SPN MCBDB with I/c:- 25 Amp DP RCBO(RCCB+MCB) 10KA & O/G :- C-curve 6-16 Amp SP MCB :- 4 Nos. For Toll booth UPS power & For Electrical Room + Medical Aid post | Nos | 36 |  |  | Panel/Switc borad/ MCB Board are required at the both toll plaza for cable renovation & Proper Load separation work.
45 | 8-Way TPN DB Board SITC of Approved make 8-Way TPN DB - Three phase incoming and single phase horizontal type outgoing Per phase isolation type (PPI) Double Door metal clad D.B. company prewired having Incoming and outgoing as mentioned below with NL suitable to operate on 415 Volt A.C. power and having overload and short circuit tripping element breaking capacity 10KA (for all MCB & ELCB) to be erected in flush type and company fabricated 16 G.M.S./ IK 08 Certificate sheet box with powder coated inside and outside after apply seven tank chemical process of M.S. sheet cover complete with suitable integral single piece construction tinned copper busbar- and link with all necessary interconnection and with neccessary size wooden board for mounting MCBDB . Manufacturer must be Provided .(1)IP 43 Protection Certificate.(2) Seven tank Powder Coating Certificate.(3) Copper/Brass make Neutral & Earthing link with Isolation and Protecting Cover. (a) For 8 Way TPN MCBDB I/c:- 63 Amp FP MCB 10KA C-63 A DP ELCB 30ma 10KA -03 nos O/G :- C-curve 6-32 Amp SP MCB :- 21 Nos. For Toll plaza - Admin building GF + FF - Lighting & Raw power DB & Toll lane TMS equipment | Nos | 6 |  |  | Panel/Switc borad/ MCB Board are required at the both toll plaza for cable renovation & Proper Load separation work.
46 | PVC PIPES 25 MM Dia Providing and erecting Medium Class FIA approved and ISI mark white colour (embossed) RIGID PVC PIPES of following size complete erected with necessary PVC fittings & Junction boxes fixed with adhesive solution & clamps on / in wall / ceiling along with continuous fish wire to draw mains with necessary fittings and junction boxes for following dia. (a) 25 mm. dia. | Rmt | 1000 |  |  | The quantity is considered approximate and will be done only if required, based on the site conditions at the time of work execution.
47 | 2 Type x 1.5 sq.mm. Single core FRLS copper PVC Insulated wire Providing and laying Mains with FRLS PVC Insulated wire ISI marked 1.1 KV grade with FIA approved ISI mark medium class 20/25/32 mm dia. embossed rigid PVC pipe with PVC fitting fixed with adhesive solution to be erected on/in brick wall / slab along with continuous G. I. fish wire to draw mains laid in approved manner with plastering by cement mortar & finishing the surface to match the wall / ceiling complete with FRLS PVC insulated wire for earth continuity. (Approved ISI make only) [a] 2 x 1.5 sq.mm. FRLS copper multi stranded conductor mains with 1.5 sq.mm. FRLS copper multi stranded conductor for earthing as per standard colour code. [conductor resistance should be as per IS:8130/1984] for Toll plaza Main Wiring | Rmt | 500 |  |  | The quantity is considered approximate and will be done only if required, based on the site conditions at the time of work execution.
48 | 2 type x 2.5 sq.mm. Single core FRLS copper flexi wire multi stranded conductor mains with 1.5 sq.mm. FRLS copper multi stranded conductor Providing and laying Mains with FRLS PVC Insulated wire ISI marked 1.1 KV grade with FIA approved ISI mark medium class 20/25/32 mm dia. embossed rigid PVC pipe with PVC fitting fixed with adhesive solution to be erected on/in brick wall / slab along with continuous G. I. fish wire to draw mains laid in approved manner with plastering by cement mortar & finishing the surface to match the wall / ceiling complete with FRLS PVC insulated wire for earth continuity. (Approved ISI make only) [b] 2 x 2.5 sq.mm. FRLS copper multi stranded conductor mains with 1.5 sq.mm. FRLS copper multi stranded conductor for earthing as per standard colour code. (Conductor resistance should be as per IS:8130/1984) | Rmt | 1500 |  |  | The quantity is considered approximate and will be done only if required, based on the site conditions at the time of work execution.
49 | 2 Type x 4.0 sq.mm. FRLS copper multi stranded conductor mains with 2.5 sq.mm. FRLS copper multi stranded conductor for earthing Providing and laying Mains with FRLS PVC Insulated wire ISI marked 1.1 KV grade with FIA approved ISI mark medium class 20/25/32 mm dia. embossed rigid PVC pipe with PVC fitting fixed with adhesive solution to be erected on/in brick wall / slab along with continuous G. I. fish wire to draw mains laid in approved manner with plastering by cement mortar & finishing the surface to match the wall / ceiling complete with FRLS PVC insulated wire for earth continuity. (Approved ISI make only) [c] 2 Type x 4.0 sq.mm. FRLS copper multi stranded conductor mains with 2.5 sq.mm. FRLS copper multi stranded conductor for earthing as per standard colour code. [conductor resistance should be as per IS:8130/1984] | Rmt | 1500 |  |  | The quantity is considered approximate and will be done only if required, based on the site conditions at the time of work execution.
50 | LED Tube Light 20-24 W 4 feet SITC Of Max 24 Watt LED Indoor Commercial make high efficiency performance Tube rod Approx. 4 feet (lamp) with combination of high quality diffused polycarbonate and alluminium base dedicated heat sink for better perfomance of LED and also long life.High quality LED must be placed on metal core printed circuit board for better heat dissipation. seprate driver with all protection like under voltage (160V to 270V) over voltage protection 2 KV surge protection.The life of lamp should have 25 000 hrs at L70 THD<15% efficiency >=110lm/w with high power factor > 0.90 with CRI > 80 for better color rendition total lumens should be min 2400. The lamp should be suitable for T8 box type fitting made form CRCA sheet and white powder coated.The data sheet of LM79 for complete lamp can also be provided (Note:-The manufacturer/ authorised Channel partner of the manufacturer has to submit 4 yr free replcement Guarantee for complete Fixture ) (Approval will be given strictly subject to item specification). | Nos | 50 |  |  | For installation Tunel with proper wiring at both toll Plaza
51 | Cable Tray 300X40X4 mm Supplying and erecting approved make GRP Perforated type Cable Tray with required GRP Straight Coupler Plates Corner etc. Material – Corrosion Resistant Polyester Flame Retardant U.V. Stabilized Resin System - Manufactured from Pultruded Sections- Polyester Resin System Glass Content : 55 – 60 % - - Standard Length : 3000mm- Support Span – 1500mm Deflection L/200 - Specification NEMA FG1 1993- UV Resistant - Flame Retardant – IS 6746 - Appendix K/UL 94 Very Low Flammability - Specification Followed NEMA FG1 1993 Oxygen Index – Minimum 30% as per ASTM D 2863 - Flame Spread (Extent of Burning) – 20mm as per Standard ASTM D 635 - Tensile Strength – 4000 – 8000 Kg/Cm2 as per Standard ASTM D 638 - Flexural Strength – 2500 – 10000 Kg/Cm2 as per Standard ASTM D 790- Izod Impact Strength – 130 Kg/Cm2 as per Standard ASTM D 256- Compressive Strength – 2500 – 5000 Kg/Cm2 as per Standard ASTM D 695- Barcol Hardness – 50 – 65. (E) Width - 300 mm Pultruded “C” Channel with 40mm Sides 4mm Thickness Loading 25 Kg./Mtr. ( Sumip coromandak Eircon Satyam -composite Make or equivalent make app by engineer in charge subject to above specification) | Rmt | 100 |  |  | For installation Tunel & near the admin building for proper cabling/dressing at both toll Plaza
52 | 8 SWG GI Earthing Wire upply & Laying Hot Deep 8 swg GI earth wire in horizontal or vertical run in ground/surface/recess including riveting soldering saddles making connection etc. as required. from Street Light Pole to pole connection & laying with Existing Armoured cable | Rmt | 32000 |  |  | For all existing Pole earthing , Panel, & highmat earthing
53 | 200A 415 Volts TPN Rewireable Cut-Out fuse units with mounting Bracket Supplying, Installing, Testing & Commissioning (SITC) of TPN Rewireable Switch Fuse Unit, rated 200 Ampere, 415 Volt AC, 50 Hz, 3-Phase, 3-Pole, complete with MS mounting bracket and accessories, suitable for outdoor highway street lighting application. The unit shall be installed after the energy meter and before the street light feeder pillar panel, complete in all respects as per specifications and site requirements.Quick make and break operation Enclosure made of CRCA sheet steel, duly pre-treated and powder coated, Hard bright tin-plated copper contacts for Terminals suitable for Aluminium and Copper conductors, Porcelain fuse carriers with fully shrouded live parts, Door interlocking facility provided for safety, Knock-outs provided at top, bottom and rear sides for cable entry Separate fuse and terminal block arrangement, Adequate internal space for wiring and maintenance PVC gasket provided for weather-proof sealing, MS mounting bracket complete with clamps, nuts and bolts | Nos | 10 |  |  | The quantity is considered approximate and will be installed only if required, based on the site conditions at the time of work execution. It will be installed after energy meter & before load or Fedeer pillar Panel
|  |  | Total |  | 0

## BOQ (hidden)
Sub:- BOQ for Electrical improvement works for Highway Street Lights & Toll Plaza submitted by Designtech MEP Consultants.
Sr. No | Specification | UOM | PR.Qty. | Rate | Value | Remark
1 | MAIN STREET LIGHT FEEDER PILLAR Complete SITC Set of Main Street Feeder Pillar as below Electrolytic grade Aluminium bus bar by means of SMC / DMC type insulator 110/220 V LED (22.5 mm dia ) R Y B ON Indicating lamp with integral circuit terminal block including connection etc. as required. Electrical insulating rubber matts confirming to IS: 15652 / 2006 with one side anti skid aberration marks and pasting the mat with synthetic rubber adhesive as required. 11 KV 2.5 mm thick with proof voltage 22 KV / 3 min. and Break Down Voltage 45 KV Current Transformer with all necessary support in existing panel including connection etc. as required . from 40/5 to 63/5 Ratio 10 VA class 1 accuracy 0.5 A to 4 A rating (Protection MCB) CT operated direct reading type Ampere meter on existing panel making connection by PVC insulated copper conductor with PVC sleeves / channel etc. as required. Below 500 A (Digital type) (0-500) V range Volt meter on existing panel making connection by PVC insulated copper conductor with PVC sleeves / channel etc. as required. Digital type selector switch of 10 A for voltmeter (4 position ) including making connection etc. as required . CT linked selector switch of 10 A for Ampere meter (4 position ) including making connection etc. as required . Totally enclosed Plinth mounted dust vermin proof double door outdoor type IP55 Feeder Pillar made out of min 3mm sheet complete complete including foundation civil and structural works INCOMING P&F 415 V AC FP MCB with positive isolation of breaking capacity not less than 10/16 KA (B/ C/ D tripping characteristic) ISI marked IS 8828(1996)]/ conforming to IEC 60898 in existing board/sheets including making connections with lugs testing etc. as required. 63 Amp 10 kA - 1 nos. OUTGOINGS P&F 240/415 V AC MCB with positive isolation of breaking capacity not less than 10 KA (B/ C/ D tripping characteristic) ISI marked IS 8828(1996)]/ conforming to IEC 60898 in existing board/sheets including making connections with lugs testing etc. as required. Double pole MCB 32 A rating ( 2 no.) Four pole MCB 6 A to 25 A rating ( 8 no.) 1no. 110 - 240 V AC 1 ph. 2 W Astronomical time switch with surge suppressor memory card Sunrise / Sunset selectable software for programming including making connection etc. as required Provide Space for energy meter in panel compartment ( Energy meter will be supplied & Installed by DISCOM ) P & F of ac operated heavy duty 230 /415 Volt power contactor conforming to IS:13947-4-1/IEC:947-4-1 having provision of mechanical interlocking auxilary contacts Din rail mounting type including making connections testing etc. as required. 4 pole Power Contactors with following AC 1 Rating 40-63 Amp. | Nos | 35 | 85000 | 2975000 | In Place of Rusted, Damaged or Missing Panel, Location wise sheet is attached for referece | This needs to be considered
2 | Digital time switch Make L&T Supplying & erecting approved make Digital time switch having lithium cell 6 years operative and operate battery backup 1 channel day clock with 14 memory programme suitable to operate on 240V + 5% 16A with floating contacts Minimum switching setup time 1 minimum & LCD display. Also comprised permanent ON/OFF switching. Programming switches & housed in fire proof thermoplastic enclosure & transparent cover erected as required with necessary connection erected as directed. | Nos |  | 5500 | 0 | The quantity is considered approximate and will be installed only if required, based on the site conditions at the time of work execution. | This can be left out for now; if the need arises in the future, it can be ordered and installed individually. | Removed from PR
3 | MCCB 100 A 4 Pole 440 V Providing and erecting Approved make Four pole moulded case circuit breaker having breaking capacity ICU of 25 KA. at 415 V having normal current rating up to 25 A to 100A. with Fixed thermal & magnetic release suitable to work on A.C. supply 50 c/s. with all internal connections spreader tinned copper & complete erected in existing 16 G.M.S. housing. ICS=100% of ICU only | Nos |  | 7500 | 0 | The quantity is considered approximate and will be installed only if required, based on the site conditions at the time of work execution. | This can be left out for now; if the need arises in the future, it can be ordered and installed individually. | Removed from PR
4 | MCB 6A-32A 2 Pole Providing & erecting 240 V MCB double pole switch for lighting Load (B Curve) having 10 KA breaking capacity & confirms to IS : 8828 in existing box having following capacity 6 to 32 Amp | Nos | 100 | 325 | 32500 | The quantity is considered approximate and will be installed only if required, based on the site conditions at the time of work execution. | Such MCBs can be used in the main feeder pillars of existing streetlights for switching the ATMS supply.
5 | MCB 40 A 2 Pole Providing & erecting 240 V MCB double pole switch for lighting Load (B Curve) having 10 KA breaking capacity & confirms to IS : 8828 in existing box having following capacity | Nos |  | 450 | 0 | The quantity is considered approximate and will be installed only if required, based on the site conditions at the time of work execution. |  | Removed from PR
6 | MCB 32A 4 Pole Providing & erecting 415V MCB Four Pole Switch for Lighting Load (B curve) having 10KA breaking capacity & confirms to IS :8828 in existing box having following capacity | Nos | 10 | 625 | 6250 | The quantity is considered approximate and will be installed only if required, based on the site conditions at the time of work execution.
7 | MCB 40A 4 Pole Providing & erecting 415V MCB Four Pole Switch for Lighting Load (B curve) having 10KA breaking capacity & confirms to IS :8828 in existing box having following capacity | Nos | 10 | 735 | 7350 | The quantity is considered approximate and will be installed only if required, based on the site conditions at the time of work execution.
8 | MCB 63A 4 Pole Providing & erecting 415V MCB Four Pole Switch for Lighting Load (B curve) having 10KA breaking capacity & confirms to IS :8828 in existing box having given capacity | Nos | 60 | 1150 | 69000 | The quantity is considered approximate and will be installed only if required, based on the site conditions at the time of work execution. | Such MCBs can be installed inside the high-mast poles during repair work; currently, the cables inside the high-mast poles at all locations are directly jointed.
9 | MCB 6A-25A 1 Pole providing and erecting Miniature circuit breaker single pole 6A to 25A suitable to operate on 240 V A.C. system and having breaking capacity 10 KA to be erected in existing box. confirming to IS 8828/1996 with ISI Mark | Nos | 1000 | 150 | 150000 | Major requirement of 1 Pole MCB required for all existing 699 No's LED light fixture (263.000, 290.600, 306.100, 314.640, 348.600, 370.700, 382.750, 403.400, 403.650, 413.850, 416.750) othar all location (Ch:-270-419) where HPSV Light fixture available in Place of Damaged/Missing MCB | For only the LED street lights quantity to be considered | 1000 Qty reduced
10 | Contactor 4 pole 440V 16 Amp. Make L&T Supplying & erecting power contactor AC3 duty for time switch complete erected as per direction Cat III | No |  | 1050 | 0 | The quantity is considered approximate and will be installed only if required, based on the site conditions at the time of work execution. | To be eliminated from BOQ | Removed from PR
11 | Contactor 4 pole 440V 63 Amp Make L&T Supplying & erecting power contactor AC3 duty for time switch complete erected as per direction Cat III | Nos | 60 | 3250 | 195000 | The quantity is considered approximate and will be installed only if required, based on the site conditions at the time of work execution.
12 | 10.0 Sq.mm ( 4 core) XLPE Aluminium Armoured Cable Make Polycab KEI RR Cable Proving & Laying XLPE insulated & P.V.C. sheathed cable of 1.1 KV grade with aluminium conductor of IS:1554 P-I / IS :7098 P - I in ground or laying HDPE / DWC pipe. Rate also includes Supplying and making one end termination with heavy duty single compression brass gland SIBG type heavy duty aluminium lugs duly crimped with crimping tool PVC tape etc for following size of Armoured PVC sheathed / XLPE aluminium conductor cable of 1100 volt grade for TMS, ATMs & Street Light at Site & Toll Plaza. | Rmt |  | 195 | 0 | It will be used for ATMS supply at site & both Toll Plaza for cable renovation in Tunnel , Location wise sheet is attached for referece | To be directed by the ATMS Team | Remove from PR, instructed by QS Team
13 | 16 Sq.mm ( 4 core) XLPE Aluminium Armoured Cable Make Polycab KEI RR Cable Proving & Laying XLPE insulated & P.V.C. sheathed cable of 1.1 KV grade with aluminium conductor of IS:1554 P-I / IS :7098 P - I in ground or laying HDPE / DWC pipe. Rate also includes Supplying and making one end termination with heavy duty single compression brass gland SIBG type heavy duty aluminium lugs duly crimped with crimping tool PVC tape etc for following size of Armoured PVC sheathed / XLPE aluminium conductor cable of 1100 volt grade, for TMS, & Street Light at Site & Toll Plaza. | Rmt | 25000 | 225 | 5625000 | The existing overhead cable installed along the roadside for street lighting is required to be replaced with a suitably rated underground cable. The current underground/overhead unarmoured cable laid at the crash barrier is of low quality and has inadequate load-carrying capacity, resulting in repeated major faults, overheating, and short-circuiting of the pole-to-pole cable. Replacing it with a properly rated underground cable will improve system reliability, prevent recurring failures, and ensure safe and efficient operation of the street lighting network. | Spare quantity considered
14 | 25 Sq.mm (4 core) XLPE Aluminium Armoured Cable Make- Polycab KEI RR Cable Proving & Laying XLPE insulated & P.V.C. sheathed cable of 1.1 KV grade with aluminium conductor of IS:1554 P-I / IS :7098 P - I in ground or laying HDPE / DWC pipe. Rate also includes Supplying and making one end termination with heavy duty single compression brass gland SIBG type heavy duty aluminium lugs duly crimped with crimping tool PVC tape etc for following size of Armoured PVC sheathed / XLPE aluminium conductor cable of 1100 volt grade for highway Street Light at Site & Toll Plaza cable renovation. | Rmt | 20000 | 275 | 5500000 | Cable is required at the toll plaza for renovation works and for the replacement of damaged cables used for street lights and high-mast lighting. The replacement cable shall be selected as per the connected electrical load and prevailing site conditions to ensure safe, reliable, and efficient operation of the lighting system. Backup sheet is attached for reference | Spare quantity considered
15 | 35 Sq.mm (4 core) XLPE Aluminium Armoured Cable Make- Polycab KEI RR Cable Proving & Laying XLPE insulated & P.V.C. sheathed cable of 1.1 KV grade with aluminium conductor of IS:1554 P-I / IS :7098 P - I in ground or laying HDPE / DWC pipe. Rate also includes Supplying and making one end termination with heavy duty single compression brass gland SIBG type heavy duty aluminium lugs duly crimped with crimping tool PVC tape etc for following size of Armoured PVC sheathed / XLPE aluminium conductor cable of 1100 volt grade for highway Street Light at Site & Toll Plaza cable renovation. | Rmt | 2000 | 325 | 650000 | Cable is required at the toll plaza for renovation works and for the replacement of damaged service cables from the transformer to the energy meter and from the energy meter to the feeder pillar, serving the street lighting and high-mast lighting systems. | Spare quantity considered
16 | 50 Sq.mm (3.5 core) XLPE Aluminium Armoured Cable Make- Polycab KEI RR Cable Proving & Laying XLPE insulated & P.V.C. sheathed cable of 1.1 KV grade with aluminium conductor of IS:1554 P-I / IS :7098 P - I in ground or laying HDPE / DWC pipe. Rate also includes Supplying and making one end termination with heavy duty single compression brass gland SIBG type heavy duty aluminium lugs duly crimped with crimping tool PVC tape etc for following size of Armoured PVC sheathed / XLPE aluminium conductor cable of 1100 volt grade for highway Street Light at Site & Toll Plaza cable renovation. | Rmt | 1000 | 375 | 375000 | Cable is required at the toll plaza for renovation works and for the replacement of damaged service cables from the transformer to the energy meter and from the energy meter to the feeder pillar, serving the street lighting and high-mast lighting systems. | Spare quantity considered
17 | 10 Sq.mm 3 core XLPE Aluminium Armoured Cable Make- Polycab KEI RR Cable Proving & Laying XLPE insulated & P.V.C. sheathed cable of 1.1 KV grade with aluminium conductor of IS:1554 P-I / IS :7098 P - I in ground or laying HDPE / DWC pipe. Rate also includes Supplying and making one end termination with heavy duty single compression brass gland SIBG type heavy duty aluminium lugs duly crimped with crimping tool PVC tape etc for following size of Armoured PVC sheathed / XLPE aluminium conductor cable of 1100 volt grade, for TMS, ATMs & Street Light power supply at Site & Toll Plaza. | Rmt |  | 165 | 0 | It will be used for ATMS supply at site & both Toll Plaza for cable renovation in Tunnel , Location wise sheet is attached for referece | To be directed by the ATMS Team | Remove from PR, instructed by Soumya Sir QS/
18 | 70 Sq.mm (3.5 core) XLPE Aluminium Armoured Cable Make- Polycab KEI RR Cable Proving & Laying XLPE insulated & P.V.C. sheathed cable of 1.1 KV grade with aluminium conductor of IS:1554 P-I / IS :7098 P - I in ground or laying HDPE / DWC pipe. Rate also includes Supplying and making one end termination with heavy duty single compression brass gland SIBG type heavy duty aluminium lugs duly crimped with crimping tool PVC tape etc for following size of Armoured PVC sheathed / XLPE aluminium conductor cable of 1100 volt grade, for highway Street Light at Site & Toll Plaza cable renovation. | Rmt | 1000 | 450 | 450000 | Cable is required at the toll plaza for renovation works and for the replacement of damaged service cables from the transformer to the energy meter and from the energy meter to the feeder pillar, serving the street lighting and high-mast lighting systems. | Spare quantity considered
19 | DWC HDPE PIPE 63 mm dia (OD-63 mm & ID-51 mm nominal) Supplying and laying of following size DWC HDPE pipe ISI marked along with all accessories like socket bend couplers etc. conforming to IS 14930 Part II complete with fitting and cutting jointing etc.direct in ground (75 cm below ground level) including excavation and refilling the trench including sand cushioning complete as required or Directly install on behind the Crash barrier of VUP / PUP / Flyover / ROB / etc. with complete accossories SS saddles nuts bolts complete as required for Cable laying pipe from pole to pole. Replace as when required, for ATMS & highway Street Light at Site & Toll Plaza cable for cable renovation. | Rmt | 10000 | 275 | 2750000 | DWC HDPE pipe is required at the toll plaza for renovation works, for Laying of ATMS supply at site and for the replacement of damaged undergrund cables from Pole to Pole. Location wise sheet is attached for referece | To be directed by the ATMS Team for HDPE Pipe | 10000 Qty Reduced
20 | DWC HDPE PIPE 100 mm Dia (OD-100 mm & ID-90 mm nominal) Supplying and laying of following size HDPE pipe ISI marked along with all accessories like socket bend couplers etc. conforming to IS 14930 Part II complete with fitting and cutting jointing etc.direct in ground (75 cm below ground level) including excavation and refilling the trench including sand cushioning complete as required or Directly install on behind the Crash barrier of VUP / PUP / Flyover / ROB / etc. with complete accossories SS saddles nuts bolts complete as required Replace as when required, | Rmt | 1500 | 775 | 1162500 | Laying of DWC HDPE pipe is required at the toll plaza for renovation works it will be laying throgh the chamaber to chamber. Location wise sheet is attached for referece
21 | HDD Work With 100 mm Dia PN6-8 grade HDPE Pipe Providing and laying / Insert HDPE pipe for HT / LT underground cable including laying jointing insertation of hdpe pipe 2 nos x 100mm dia and 6 mm thickness without damaging surface / Road by using horizontal auger guided boring / Horizontal directional drilling machine by push and loop method. Insert of hdpe pipe in side Road boundary by cut and fill method. Rate are included with Providing and supply of hdpe pipe - 2 nos x 100mm dia. | Rmt | 1500 | 3250 | 4875000 | Laying of DWC HDPE pipe is required at the toll plaza for renovation works it will be laying . Location wise sheet is attached for referece | Quantity to be considered as per layout plan' | 500 mtr length reduced from PR | UOM Revised
22 | HDD Work With 100 mm or 63 mm Dia PN6-8 grade HDPE Pipe Providing and laying / Insert HDPE pipe for HT / LT underground cable including laying jointing insertation of hdpe pipe 1 Nos x 100 mm dia or 1 nos x 63mm dia and 6 mm thickness without damaging surface / Road by using horizontal auger guided boring / Horizontal diractional drilling machine by push and loop method.Insert of hdpe pipe in side Road boundary by cut and fill method. Rate are included with Providing and supply of hdpe pipe - 1 nos x 63mm dia. | Rmt | 1000 | 2500 | 2500000 | Laying of DWC HDPE pipe is required at the toll plaza for renovation works it will be laying . Location wise sheet is attached for referece | To be directed by the ATMS Team | 500 mtr length reduced from PR | UOM Revised
23 | Birck Wall Electrical Chamber with Cover Constructing brick masonry manhole / Chamber in cement mortar 1:4 ( 1 cement : 4 coarse sand ) with R.C.C. top slab with 1:1.5:3 mix (1 cement : 1.5 coarse sand (zone-III) : 3 graded stone aggregate 20 mm nominal size) foundation concrete 1:4:8 mix (1 cement : 4 coarse sand (zone-III) : 8 graded stone aggregate 40 mm nominal size) inside plastering 12 mm thick with cement mortar 1:3 (1 cement : 3 coarse sand) finished with floating coat of neat cement and making channels in cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) finished with a floating coat of neat cement complete as per standard design : Inside size 1200x900 mm and 900 mm deep including C.I. cover with frame (medium duty) 500 mm internal diameter total weight of cover and frame to be not less than 116 kg (weight of cover 58 kg and weight of frame 58 kg) : | Nos | 32 | 26000 | 832000 | at the toll plaza for cable renovation works , the cable will be laying throgh the chamaber to chamber. Location wise sheet is attached for referece
24 | GI Chemical Earthing Providing Fixing & Testing of Maintenance free Gel Earthing with Pipe in Strip Technology filled with anti-corrosive conductive compound (CPRI Tested) below the ground in 150 - 200 mm dia. earth pit & surrounding filled with required mineral filling compound (MFC should have hygroscopic property to retain the moisture for long time to create low resistance zone) and C.C. finished chamber covered with hinged type with locking arrangement C.I. Cover C.I. Frame of size 300mm x 300mm complete testing of earth resistance as required. of following sizes. With Pipe in Strip Technology (Inner pipe dia. / Outer pipe dia. ) 80 - 100-micron GI Coating.GI Pipe 2000 mm Long 50 / 25mm Terminal 12 mm GI Strip. For highway street Light High mast Pole & Panel earthing as per site requirement | Nos | 400 | 4500 | 1800000 | For Street Light pole & Panel, highmast Pole & Panel body earthing at site
25 | Copper Chemical electrode 50X3000 MM Earthing Work for Neutral & Body earthing of essential Electrical Equipment (Transformer VCB Cubical energy Meter DG & etc at Toll Plaza. SITC of Maintenance Free Copper Chemical electrode (99.9 % Pure) as per standard IS 3043:1987 inclusive of Manpower Material Machinery with the following specifications: (a) Copper Chemical electrode 50X3000 MM. (b) GI Mess Pipe 40X2000 mm (c) Copper Strip: 25X3 MM from earthing electrode to nearest Electrical Equipment. (d) Bentonite Powder /Charcole & Salt mixture 25 kg for every earthing pit/ As needed. (e) Heavy Duty Earthing Chamber (HDPE Square Type) Earthing Chamber having dimensions 300mmX300X260mm with concereting of Chamber for every earth Pit. (f) The Value of each earthing should be less than 3 Ohm. It will be the responsibility of contactor/ agency to pour appropriate quantity of water in all the earthing during the work of each earthing. | Nos | 16 | 10500 | 168000 | Provision for body earthing and neutral earthing shall be made for essential electrical equipment. The location-wise earthing details sheet is enclosed herewith for reference.
26 | GI Chemical electrode 50X3000 MM Earthing work for Body earthing of Electrical Equipment at Toll Plaza SITC of Maintenance Free GI Chemical electrode as per standard IS 3043:1987 inclusive of Manpower Material Machinery with the following specifications: (a) GI Chemical electrode 50X3000 MM. (b) GI Mess Pipe 40X2000 mm. (c) GI Strip: 25X3 mm from earthing electrode to nearest Electrical Equipment. (d) Bentonite Powder /Charcoal & Salt mixture 25 kg for every earthing pit / As needed. (e) Heavy Duty Earthing Chamber (HDPE Square Type) Earthing Chamber having dimensions 300mmX300X260mm with concreting of Chamber for every earth Pit. (f) The Value of each earthing should be less than 3 Ohm. (g) It will be the responsibility of contactor/ agency to pour appropriate quantity of water in all the earthing during the work of each earthing. | Nos | 56 | 6500 | 364000 | For electrical equipment body earthing Location wise sheet is attached for referece
27 | Vertical Air Termination / Lightning Arrester for electrical Building SITC of Vertical Air Termination Solid aluminium with Base- 10 mm dia and 1000 mm long. Air Termination Base tested for conditioning; Ageing Test & Lightning impulse current withstand test: 100 kA of 10/350µs waveform in an accredited Third party laboratory as per 6.3 & 6.4 of IEC 62561-1 2017 protocol with MAST 34mm dia Cold Galvanized. complete with all mounting post clamps nuts bolts insulators etc. | Nos | 2 | 9500 | 19000 | For Both Toll Electrical Building
28 | GI Earthing Strips Supply & Laying Hot Deep required size GI earth strip in horizontal or vertical run in ground/surface/recess including riveting soldering saddles making connection etc. as required. | NOS | 1800 | 110 | 198000 | For electrical equipment body earthing Location wise sheet is attached for referece
29 | Copper Earthing Strips Supply & Laying required size Copper strip in horizontal or vertical run in ground/surface/recess including riveting soldering saddles making connection etc. as required. | NOS | 150 | 1500 | 225000 | Provision for body earthing and neutral earthing shall be made for essential electrical equipment. The location-wise earthing details sheet is enclosed herewith for reference.
30 | Copper Flexi cable 70 sq. mm Supply & fixing of 70 sq.mm PVC insulated Copper flexible cable as down conductor complete install with saddles/clamps. | Rmt | 150 | 350 | 52500 | For Both Toll Plaza LA earthing for Electrical Building
31 | Lightning Strike Counter SITC of Lighting counter - To count no of lightning strike & it can record the date and time of the lightning having plastic encloser IP-65. Measuring Range: 0-100 KA Display: LCD-with 0-999 count operating temprature: -20 to 60 degree celcius No odsensor:1 nos (JEF CAPE DEHN OBO Better Man make) | Nos | 2 | 3000 | 6000 | For Both Toll Plaza LA earthing for Electrical Building
32 | 10 Mtr. GI Octagonal Street Light Pole Supply installation testing & commissioning of 10 mtr Supply and installation (Excluding foundation work) of 10 m ( clear pole height is 10 mtr. from road surface On main carriage Way. Long 70 mm Top X 175mm bottom dia 3 mm thickness Octagonal poles. Made from CR sheet steel. The pole should be made as per IS. and shall be coated with hot dip galvanizing as per IS 2629/4759. with required base plate suitable suspend local wind speed ( 140 km/Hr) and pole base is heavy MS plate welded with pole bottom with M 24 x 750 long ’J’ type EN 8 grade foundation bolts along with template for the above poles.with Rate includes (a) Supply & erection of Bakelite sheet with 2 no. 6A SP MCB & External surge protector - 20 kV & stud type terminal block suitable upto 4Cx35 sq. mm Cable. (b) Supply & Installation of 3Cx1.5 sq. Cu Flexible FRLS Wire for connection of light fitting.( From Pole JB to light fixtures ) (C) Spiral Earthing ( If ground Available ) for each streetlight pole complete with 8 SWG galvanized wire having 5 feet deep in ground and 1 feet spiral portion covered by salt coal etc. or Connect earthing through cable steel / wire armoured only. (D) For Earthing if ground is not available In that case Pole earthing on flyover / ROB / VUP / PUP etc will be by laying 8 SWG GALVANISED wire along with pole to pole cables from feeder pillars. | Nos | 100 | 22500 | 2250000 | For Damaged street Light pole repacement , details sheet is enclosed herewith for reference.
33 | Copper Flexi Cable 3X1.5 Sq. mm Supply & Installation of 3Cx1.5 sq. Cu Flexible FRLS Wire for connection of light fitting. ( From Pole Junction Box to light fixtures) | Rmt | 12000 | 65 | 780000 | ( From Pole Junction Box to light fixtures), details sheet is enclosed herewith for reference. | Spare quantity considered
34 | Single Arm 1.0 Mtr 10 Degree Supply Installation Testing & Commissioning of 1.0 mtr. long & 10-degree Tilt angle Hot dip galvanised Single Arm bracket made up of 40NB dia GI pipe suitable to mount on TOP of pole having top 70mm A/F or as per existing pole top pipe diameter. | Nos | 20 | 1150 | 23000 | For Damaged street Light pole repacement , details sheet is enclosed herewith for reference. | 100 arms to be considered as per pole instead 90 arms are taken
35 | Double Arm 2 Mtr. 16 Degree Supply Installation Testing & Commissioning of 2 mtr long & 16-degree Tilt angle hot dip galvanised Single Arm bracket made up of 40NB Dia GI pipe suitable to mount on Side of pole on Service Roadside (Differential Arm pole) | Nos | 30 | 1500 | 45000 | For Damaged street Light pole repacement , details sheet is enclosed herewith for reference. |  | 10 No's Qty Increased as par 100 No's Pole
36 | Double Arm 2.5 mtr 10 Degree Supply Installation Testing & Commissioning of 2.5 mtr. Long & 10 degree Tilt Angle hot dip galvanised Double Arm bracket made up of 40NB dia GI pipe suitable to mount on TOP of pole having top 70mm A/F or as per existing pole top pipe diameter. | Nos | 50 | 2500 | 125000 | For Damaged street Light pole repacement , details sheet is enclosed herewith for reference.
37 | RCC Foundation (M20) for 10 Mtr Octagonal Pole RCC Foundation (M20) for 10 Mtr Octagonal Pole Providing of RCC Foundation (M20) Foundation Size: 600mm x 600mm x 1200 mm. with bolts 4 nos of octagonal pole including excavation of pole pit. The scope shall also include grouting of foundation bolts including watering and ramming & provision for passage of cable by using suitable size GI pipe / DWC pipe / HDPE pipe. Vendor submit the civil foundation details from structure consultants for approval from IE / Client Note:- If the any existing foundation is found suitable for installation of the new pole the same will be used after approval and construction of new foundation will not be required. | Nos | 100 | 2200 | 220000 | For Damaged street Light pole repacement , details sheet is enclosed herewith for reference. | Drawing & UOM to be revised | Drawing sent
38 | L Bracket with Fastener/ Bolt for 10 mtr Octagonal Street Light Pole SITC of MS wall mounted steel bracket on RE wall to rest streetlight octagonal pole incl. Hilti make fastener. Contractor shall have to submit structural design for the same. Vendor submit the MS Foundation bracket details from structure consultants for approval from IE / Client | Nos | 20 | 3500 | 70000 | Some poles at Km 295 and Km 403 are hanging due to improper fixing and require re-fixing to ensure proper alignment and structural stability.
39 | 200W LED STREET LIGHT FOR MAIN CARRIAGEWAY LIGHTING + SERVICE ROAD LIGHTING SITC of 200W SMD LED Streetlight fixture with System efficacy of 135 lm/W (27000 lumens). Luminaire shall be made up of pure polyester powder coated die cast Aluminium housing with IP rated high purity Polycarbonate lens . The luminaire should have a dimension of 417mm x 285mm x 2mm ± 2mm appoximate weight of 3.8 Kg ± 0.25 Kg. The housing should be made of LM6/ADC12 Alloy non-corrosive Single Piece pressure die-cast aluminum to withstand extreme environments. All external hardware must be of SS304 grade. Luminaire shall be designed with street optic LENS for uniform light distribution. Maximum LENS dome top temperature shall be less than 95°C at 45°C ambient temperature. LM 80-08 compliant LEDs of EMC/ceramic package of wattage of 4W-5W from reputed makes such as Nichia/Cree/ Bridgelux/ Lumiled/ Osram/Seoul should be provided. LEDs used in the product shall comply with EN 62471 for Photo-biological safety and certificate for the same from manufacturer shall be provided. Luminaire shall be with IP66 and IK10 protection. The LED shall be compliant with LM80-08 standard with L70 life of 50000 Hrs tested at maximum current (Complete LM 80 test report for LED should be submitted for 10000 hrs of testing). The LEDs used should be with CCT of 5700 K CRI of Minimum 70 and SDCM of < 5. LEDs must be driven at max 70% of the rated current. MCPCB with Aluminium core and copper thickeness of 35 micron to be used for LED mounting. LED Driver shall be silicone potted Integrated type Isolated Constant Current with range 140-280V AC. Driver Efficiency > 88% & 4 KV internal surge protection with additional 10KV SPD mounted inside the luminaire and firmly fixed to the housing Power factor greater than 0.95 and total harmonic distortion (THD) of less than 10% should be integral to the luminaire. LED Driver must have short circuit open circuit Auto cut-off protection for low and high input voltage. Driver must have 440V input voltage protection for 8 hours. LED driver should have over temperature protection. Manufacturer shall have inhouse lab approved by NABL or ministry of science of govt of India. LM 79 and LM80 reports need to be submitted from a NABL/UL accredited lab to verify above parameters. Compliance to Indian Standards of IS10322 Part 5 / Sect 3:2013; 16105 : 2012; IS 16106 : 2012; IS 15885 (Part2/Sec13) : 2012; IS 16108 : 2012. Make-Wipro/Philips/Bajaj/Crompton/Havells Safely removing and shifting old fixtures, and depositing them in writing at the toll plaza or store, etc. | Nos | 2550 | 7250 | 18487500 | Required Total installation of 200 W LED Light fixture in place of 400W HPSV , details sheet is enclosed herewith for reference.
40 | Wallmounted 80 W LED Flood Street Light FOR UNDERNEATH VUP LIGHTING SITC of 80 W LED High bay light having min system lumen output of 10500. Min system Efficacy should be > 130 Lm/w. Housing Should be made up of Al die cast having High Transmittance Polycarbonate cover. Luminaire should be IP66 and IK08 Protected. Luminaire should have proper Heat sink for thermal management with eye bolt mounting. Luminaire should have beam angle of 110 Deg Wide beams for proper light distribution CRI > 80 SDCM < 5 with lifeclass of 50000 Hrs @L70B50.. Driver use should be of potted and encapsulated only. Operating voltage range of driver should be of 140 – 270 VAC with 4 KV internal surge protection THD < 10% PF > 0.95 High voltage cut off & Auto restart @ 320 VAC Phase to phase 440 V Protection for 8 Hrs. Driver should be of reputed makes such as Philips Xitanium / Osram / Meanwell only. Driver & luminaire both should be BIS Approved only. Luminaire should be tested under NABL Accredited Lab for LM79/LM80/TTC. Similar to Philips BY225P LED100S CW WB PSU FG GR | Nos | 210 | 4250 | 892500 | Location for underpass lighting details sheet is enclosed herewith for reference.
41 | Highmast Repairing Supply & Laying of raising lowering system comprising double drum winch 6 / 8 mm diameter SS wire rope trailing cable connector integral power tool motor manual handle junction box lightening finial. | Nos | 30 | 25000 | 750000 | The quantity is considered approximate and will be done only if required, based on the site conditions at the time of work execution. | Total number of highmast to be repaired is 64. But the quantity to be revised as 10 Nos Highmast | 20 Qty reduced | UOM Revised
42 | Aviation lamp for High mast SITC of LED type double dome aviation obstruction light for 30 Mtr Highmast. | Nos | 30 | 1500 | 45000 | The quantity is considered approximate and will be done only if required, based on the site conditions at the time of work execution.
43 | Re-installation of High mast pole when required Erection of the high mast with the help of suitable tools and plants wiring of luminaries with all wiring materials like PVC insulated PVC sheathed flexible cable of suitable copper conductor cores of 1.5 sq. mm lugs MCB and all labour as a complete job. Rate include cranes for using lowering & re-installation of High mast pole. | Nos | 10 | 25000 | 250000 | The quantity is considered approximate and will be done only if required, based on the site conditions at the time of work execution. |  |  | UOM Revised
44 | HIGH MAST FEEDER PANEL 30 Mtr Highmast SITC of outdoor stand mounted feeder pillar with 40A TPN MCB incomer single dial time switch 40A FP contactor for the automatic switching of luminaries power tool control with 2 no 9A contactors and raise lower push button Incoming 35 sq. mm and out going 20 x1.5 sq. mm terminals. (4) Construction of shallow foundation with M20 grade concrete for the highmast considering the safe soil bearing capacity at site as 10 T/sqmtr at 2 metre depth with all materials and labour. (Foundation civil design will be approved by structural consultants). | Nos | 35 | 20000 | 700000 | Location for installation of Highmast Control Panel details sheet is enclosed herewith for reference.
45 | 400 WATT LED LIGHTING FIXTURES FOR HIGH MAST @ ALL JUNCTIONS + GRADE SEPARATED JUNCTIONS ETC. SITC of 400W SMD LED Floodlight fixture with System efficacy of 125 lm/W (50000 lumens). Luminaire shall be made up of LM6/ADC12 Alloy non-corrosive pure polyster power coated die cast Aluminium housing with PC lens. Lumianire should be of dimension 319mm x 507mm x 97mm height ± 5mm height and the approximate weight should be within the 12.0Kg ± 0.5Kg. Luminaire should be available with 25° and 60° beam angle option. Luminaire should be made of four individual modules of 100W to 125W each. All external hardware must be of SS304 grade. LM 80-08 compliant LEDs of EMC/ceramic package of wattage of 5W from reputed makes such as Nichia/Cree/ Bridgelux/ Lumiled/ Osram/Seoul should be provided. LEDs used in the product shall comply with EN 62471 for Photo-biological safety and certificate for the same from manufacturer shall be provided. Maximum LENS dome top temperature shall be less than 95°C at 45°C ambient temperature. Luminaire shall be with IP66 and IK07 protection. It should be cabable to operating under ambient temperature range of -10°C to +45°C. The LED shall be compliant with LM80-08 standard with L70 life of 50000 Hrs tested at maximum current (Complete LM 80 test report for LED should be submitted for 10000 hrs of testing). The LEDs used should be with CCT of 5700 K CRI of Minimum 70 and SDCM < 5. LEDs must be driven at max 70% of the rated current. MCPCB with Aluminium core and copper thickeness of 35 micron to be used for LED mounting. LED Driver shall be silicone potted Integrated type Isolated Constant Current with range 140-280V AC. Driver Efficiency > 88% & 4 KV internal surge protection with additional 10KV SPD mounted inside the luminaire and firmly fixed to the housing Power factor greater than 0.95 and total harmonic distortion (THD) of less than 10% should be integral to the luminaire. LED Driver must have short circuit open circuit Auto cut-off protection for low and high input voltage. LED driver should have 440V AC protection for atleast 8 hours.LED driver should have over temperature protection.Individual drivers should be provided with individual modules along with ventilated enclousure to hide the wirings. Driver must be with Aluminium casing. Manufacturer shall have inhouse lab approved by NABL or ministry of science of govt of India. LM 79 and LM80 reports need to be submitted from a NABL/UL accredited lab to verify above parameters. Compliance to Indian Standards of IS10322 Part 5 / Sect 5:1967; 16105 : 2012; IS 16106 : 2012; IS 15885 (Part2/Sec13) : 2012; IS 16108 : 2012. | Nos | 510 | 13500 | 6885000 | Location for installation/replacement of Highmast LED Light fixture in Place of HPSV Fixture, details sheet is enclosed herewith for reference. | 7 numbers of spare is considerd in the qty
46 | Internal Electrical Wiring (Lighting Circuit) for Toll Plaza :- Providing and erecting Point wiring with 1.1 KV grade ISI marked 2 X 1.5 sq. mm copper PVC insulted FRLS wire with 1.5 sq. mm (green) copper PVC insulated FRLS wire for earth continuity in FIA approved ISI mark medium class white colour 20/25 mm dia. embossed rigid PVC pipe with PVC fitting fixed with adhesive solution erected on/in Brick Wall / slab along with continuous G.I. fish wire to draw wires and laid in approved manner zari for PVC pipe and boxes shall be filled with cement mortar and finishing the surface to match the wall / ceiling complete with approved make 5/6 Amp. ISI make modular type switch and accessories mounted in 20 G. G.I. company fabricated metallic box covered with appropriate front plate modules erected flushed with wall / ceiling with necessary modular lamp holder / modular ceiling rose / HD Connector (make & model approved by EIC and matching colur with switches accessories) (Deep Junction box 75mm depth if required) as directed for concealed wiring. Light point. Necessary sheet / tape / polythene / sand must be erected or filled in all box to prevent mortar going into the box. Length of point wiring must not increase than 10 mtr. For that necessary switch boards and their locations must be finalised before execution by agency otherwise payment will not be done for extra long point. (For future extention if required agency has to erect one higher size metal box and modular plate as per instruction of EIC. Cost of blank plate shall be paid as per tender item) [This item include cleaning (inside/outside) of all G.I. switch boards electric point box fan box MCBDB & box cutting plaster finishing for modular plate without any gap] [conductor resistance should be as per IS:8130/1984] | NOS | 100 | 750 | 75000 | The quantity is considered approximate and will be done only if required, based on the site conditions at the time of work execution.
47 | Internal Electrical power Wiring for Toll Plaza :- Providing and fixing Plug Point wiring with 1.1 KV grade ISI marked approved make 2 x 2.5 sq.mm copper PVC insulated FRLS wire with 1.5 sq.mm (green) copper PVC insulated FRLS wire for earth continuity in FIA approved ISI mark white colour medium class 20/25 mm dia. embossed rigid PVC pipe with PVC fitting fixed with adhesive solution erected in wall/slab along with continuous G. I. fish wire to draw wires and laid in approved manner zari for PVC pipe & boxes shall be filled with cement mortar & finishing the surface to match the wall / ceiling complete with 16 Amp Modular type Swich and accessories mounted in 20 G. GI company fabricated metallic box covered with appropriate front plate modules erected flushed with wall. (a) 16 Amp. Indicator switch & 1 No. 6/16 A universal socket white colour suitable for 3/5 pin top duly both having ISI mark. (Necessary sheet / tape / polythene / sand must be erected or filled in all box To Prevent Mortor Going In To The Box) (Conductor resistance should be as per IS:8130/1984) ( FOR POWER PLUG IN BOOTH & ADMIN BUILDING ) | NOS | 40 | 1550 | 62000 | The quantity is considered approximate and will be done only if required, based on the site conditions at the time of work execution.
48 | Power Wiring for (A.C POINT / BLOWER ONLY FOR BOOTH & ADMIN BUILDING) Providing & Erecting Plug Point wiring with approved ISI marked 1.1 kv grade 2 x 4.0 sq.mm copper PVC insulated FRLS wire with 2.5 sq.mm (green) copper PVC insulated FRLS wire for earth continuity in FIA approved ISI mark white colour medium class 25 mm dia. embossed rigid PVC pipe with PVC fitting fixed with adhesive solution erected in wall / slab along with continuous G.I. fish wire to draw wires and laid in approved manner. zari for PVC pipe & boxes shall be filled with cement mortar & finishing the surface to match the wall / ceiling complete with approved make 20 Amp. Modular type indicator switch and accessories mounted in 20 SWG GI company fabricated metallic box covered with appropriate front plate modules erected flushed with wall / ceiling. (a) 20 Amp Indicator switch & 1 No. 20 A universal socket white colour suitable for 3 pin top duly both having ISI mark(A.C POINT / BLOWER ONLY FOR BOOTH & ADMIN BUILDING ) (Necessary sheet / tape / polythene / sand must be erected or filled in all box to Prevent Mortor Going In to The Box) the quantity will be consider in set/point. | NOS | 60 | 1850 | 111000 | The quantity is considered approximate and will be done only if required, based on the site conditions at the time of work execution.
49 | Surge Protection Device (SPD) Supply Installation Testing & Commissioning of Three Phase 440 V Surge Suppressor protection Device (SPD) & 40 Amp TPN MCB (or As per SPD OEM guide line for the protection of SPD which is erected such a way that it can be operated easily) SPD must be capable to protect all electrical and electronics equipments if SPD blast or fuse then the panel builder must have replace it soon during defect liability period. (Hakel ikra OBBO make) (With Three year Gaurantee/warranty) | Nos | 6 | 3500 | 21000 | For Electrical equipment safety, It will be installed in 1 No's in Admin building & 2 No's in SWB Building at both toll plaza
50 | 6-Way SPN DB Board Double Door SITC of Approved make 6-Way SPN Double Door metal clad D.B. company prewired having Incoming and outgoing as mentioned below with NL suitable to operate on 230 Volt A.C. power and having overload and short circuit tripping element breaking capacity 10KA (for all MCB & ELCB) to be erected in flush type and company fabricated 16 G.M.S./ IK 08 Certificate sheet box with powder coated inside and outside after apply seven tank chemical process of M.S. sheet cover complete with suitable integral single piece construction tinned copper busbar- and link with all necessary interconnection and with neccessary size wooden board for mounting MCBDB . Manufacturer must be Provided .(1)IP 43 Protection Certificate.(2) Seven tank Powder Coating Certificate.(3) Copper/Brass make Neutral & Earthing link with Isolation and Protecting Cover. (a) For 6 Way SPN MCBDB with I/c:- 25 Amp DP RCBO(RCCB+MCB) 10KA & O/G :- C-curve 6-16 Amp SP MCB :- 4 Nos. For Toll booth UPS power & For Electrical Room + Medical Aid post | Nos | 36 | 7500 | 270000 | Panel/Switch borad/ MCB Board are required at the both toll plaza for cable renovation & Proper Load separation work. 16 Toll booth tunnels & 2 extra taken for other equipment for each Toll Plaza
51 | 8-Way SPN Distribution Board Double Door SITC of Approved make 8-Way SPN Double Door metal clad D.B. company prewired having Incoming and outgoing as mentioned below with NL suitable to operate on 230 Volt A.C. power and having overload and short circuit tripping element breaking capacity 10KA (for all MCB & ELCB) to be erected in flush type and company fabricated 16 G.M.S./ IK 08 Certificate sheet box with powder coated inside and outside after apply seven tank chemical process of M.S. sheet cover complete with suitable integral single piece construction tinned copper busbar- and link with all necessary interconnection and with neccessary size wooden board for mounting MCBDB . Manufacturer must be Provided .(1)IP 43 Protection Certificate.(2) Seven tank Powder Coating Certificate.(3) Copper/Brass make Neutral & Earthing link with Isolation and Protecting Cover. (a) For 6 Way SPN MCBDB with I/c:- 32 Amp DP RCBO(RCCB+MCB) 10KA & O/G :- C-curve 6-20 Amp SP MCB :- 6 Nos. | NOS |  | 8750 | 0 | Panel/Switc borad/ MCB Board are required at the both toll plaza for cable renovation & Proper Load separation work. | To be removed from BOQ | Removed from PR
52 | 8-Way TPN DB Board SITC of Approved make 8-Way TPN DB - Three phase incoming and single phase horizontal type outgoing Per phase isolation type (PPI) Double Door metal clad D.B. company prewired having Incoming and outgoing as mentioned below with NL suitable to operate on 415 Volt A.C. power and having overload and short circuit tripping element breaking capacity 10KA (for all MCB & ELCB) to be erected in flush type and company fabricated 16 G.M.S./ IK 08 Certificate sheet box with powder coated inside and outside after apply seven tank chemical process of M.S. sheet cover complete with suitable integral single piece construction tinned copper busbar- and link with all necessary interconnection and with neccessary size wooden board for mounting MCBDB . Manufacturer must be Provided .(1)IP 43 Protection Certificate.(2) Seven tank Powder Coating Certificate.(3) Copper/Brass make Neutral & Earthing link with Isolation and Protecting Cover. (a) For 8 Way TPN MCBDB I/c:- 63 Amp FP MCB 10KA C-63 A DP ELCB 30ma 10KA -03 nos O/G :- C-curve 6-32 Amp SP MCB :- 21 Nos. For Toll plaza - Admin building GF + FF - Lighting & Raw power DB & Toll lane TMS equipment | Nos | 6 | 22500 | 135000 | Panel/Switc borad/ MCB Board are required at the both toll plaza for cable renovation & Proper Load separation work.
53 | PVC PIPES 25 MM Dia Providing and erecting Medium Class FIA approved and ISI mark white colour (embossed) RIGID PVC PIPES of following size complete erected with necessary PVC fittings & Junction boxes fixed with adhesive solution & clamps on / in wall / ceiling along with continuous fish wire to draw mains with necessary fittings and junction boxes for following dia. (a) 25 mm. dia. | Rmt | 1000 | 35 | 35000 | The quantity is considered approximate and will be done only if required, based on the site conditions at the time of work execution.
54 | 2 Type x 1.5 sq.mm. Single core FRLS copper PVC Insulated wire Providing and laying Mains with FRLS PVC Insulated wire ISI marked 1.1 KV grade with FIA approved ISI mark medium class 20/25/32 mm dia. embossed rigid PVC pipe with PVC fitting fixed with adhesive solution to be erected on/in brick wall / slab along with continuous G. I. fish wire to draw mains laid in approved manner with plastering by cement mortar & finishing the surface to match the wall / ceiling complete with FRLS PVC insulated wire for earth continuity. (Approved ISI make only) [a] 2 x 1.5 sq.mm. FRLS copper multi stranded conductor mains with 1.5 sq.mm. FRLS copper multi stranded conductor for earthing as per standard colour code. [conductor resistance should be as per IS:8130/1984] for Toll plaza Main Wiring | Rmt | 500 | 85 | 42500 | The quantity is considered approximate and will be done only if required, based on the site conditions at the time of work execution.
55 | 2 type x 2.5 sq.mm. Single core FRLS copper flexi wire multi stranded conductor mains with 1.5 sq.mm. FRLS copper multi stranded conductor Providing and laying Mains with FRLS PVC Insulated wire ISI marked 1.1 KV grade with FIA approved ISI mark medium class 20/25/32 mm dia. embossed rigid PVC pipe with PVC fitting fixed with adhesive solution to be erected on/in brick wall / slab along with continuous G. I. fish wire to draw mains laid in approved manner with plastering by cement mortar & finishing the surface to match the wall / ceiling complete with FRLS PVC insulated wire for earth continuity. (Approved ISI make only) [b] 2 x 2.5 sq.mm. FRLS copper multi stranded conductor mains with 1.5 sq.mm. FRLS copper multi stranded conductor for earthing as per standard colour code. (Conductor resistance should be as per IS:8130/1984) | Rmt | 1500 | 160 | 240000 | The quantity is considered approximate and will be done only if required, based on the site conditions at the time of work execution.
56 | 2 Type x 4.0 sq.mm. FRLS copper multi stranded conductor mains with 2.5 sq.mm. FRLS copper multi stranded conductor for earthing Providing and laying Mains with FRLS PVC Insulated wire ISI marked 1.1 KV grade with FIA approved ISI mark medium class 20/25/32 mm dia. embossed rigid PVC pipe with PVC fitting fixed with adhesive solution to be erected on/in brick wall / slab along with continuous G. I. fish wire to draw mains laid in approved manner with plastering by cement mortar & finishing the surface to match the wall / ceiling complete with FRLS PVC insulated wire for earth continuity. (Approved ISI make only) [c] 2 Type x 4.0 sq.mm. FRLS copper multi stranded conductor mains with 2.5 sq.mm. FRLS copper multi stranded conductor for earthing as per standard colour code. [conductor resistance should be as per IS:8130/1984] | Rmt | 1500 | 195 | 292500 | The quantity is considered approximate and will be done only if required, based on the site conditions at the time of work execution.
57 | LED Tube Light 20-24 W 4 feet SITC Of Max 24 Watt LED Indoor Commercial make high efficiency performance Tube rod Approx. 4 feet (lamp) with combination of high quality diffused polycarbonate and alluminium base dedicated heat sink for better perfomance of LED and also long life.High quality LED must be placed on metal core printed circuit board for better heat dissipation. seprate driver with all protection like under voltage (160V to 270V) over voltage protection 2 KV surge protection.The life of lamp should have 25 000 hrs at L70 THD<15% efficiency >=110lm/w with high power factor > 0.90 with CRI > 80 for better color rendition total lumens should be min 2400. The lamp should be suitable for T8 box type fitting made form CRCA sheet and white powder coated.The data sheet of LM79 for complete lamp can also be provided (Note:-The manufacturer/ authorised Channel partner of the manufacturer has to submit 4 yr free replcement Guarantee for complete Fixture ) (Approval will be given strictly subject to item specification). | Nos | 50 | 650 | 32500 | For installation Tunel with proper wiring at both toll Plaza
58 | Cable Tray 300X40X4 mm Supplying and erecting approved make GRP Perforated type Cable Tray with required GRP Straight Coupler Plates Corner etc. Material – Corrosion Resistant Polyester Flame Retardant U.V. Stabilized Resin System - Manufactured from Pultruded Sections- Polyester Resin System Glass Content : 55 – 60 % - - Standard Length : 3000mm- Support Span – 1500mm Deflection L/200 - Specification NEMA FG1 1993- UV Resistant - Flame Retardant – IS 6746 - Appendix K/UL 94 Very Low Flammability - Specification Followed NEMA FG1 1993 Oxygen Index – Minimum 30% as per ASTM D 2863 - Flame Spread (Extent of Burning) – 20mm as per Standard ASTM D 635 - Tensile Strength – 4000 – 8000 Kg/Cm2 as per Standard ASTM D 638 - Flexural Strength – 2500 – 10000 Kg/Cm2 as per Standard ASTM D 790- Izod Impact Strength – 130 Kg/Cm2 as per Standard ASTM D 256- Compressive Strength – 2500 – 5000 Kg/Cm2 as per Standard ASTM D 695- Barcol Hardness – 50 – 65. (E) Width - 300 mm Pultruded “C” Channel with 40mm Sides 4mm Thickness Loading 25 Kg./Mtr. ( Sumip coromandak Eircon Satyam -composite Make or equivalent make app by engineer in charge subject to above specification) | Rmt | 100 | 750 | 75000 | For installation Tunel & near the admin building for proper cabling/dressing at both toll Plaza
59 | 8 SWG GI Earthing Wire upply & Laying Hot Deep 8 swg GI earth wire in horizontal or vertical run in ground/surface/recess including riveting soldering saddles making connection etc. as required. from Street Light Pole to pole connection & laying with Existing Armoured cable | Rmt | 32000 | 15 | 480000 | For all existing Pole earthing , Panel, & highmast earthing |  | 20000 qty reduced
60 | 200A 415 Volts TPN Rewireable Cut-Out fuse units with mounting Bracket Supplying, Installing, Testing & Commissioning (SITC) of TPN Rewireable Switch Fuse Unit, rated 200 Ampere, 415 Volt AC, 50 Hz, 3-Phase, 3-Pole, complete with MS mounting bracket and accessories, suitable for outdoor highway street lighting application. The unit shall be installed after the energy meter and before the street light feeder pillar panel, complete in all respects as per specifications and site requirements.Quick make and break operation Enclosure made of CRCA sheet steel, duly pre-treated and powder coated, Hard bright tin-plated copper contacts for Terminals suitable for Aluminium and Copper conductors, Porcelain fuse carriers with fully shrouded live parts, Door interlocking facility provided for safety, Knock-outs provided at top, bottom and rear sides for cable entry Separate fuse and terminal block arrangement, Adequate internal space for wiring and maintenance PVC gasket provided for weather-proof sealing, MS mounting bracket complete with clamps, nuts and bolts | Nos | 10 | 15000 | 150000 | The quantity is considered approximate and will be installed only if required, based on the site conditions at the time of work execution. It will be installed after energy meter & before load or Fedeer pillar Panel
|  |  | Total |  | 64531600
74967100
10435500

## 1-Distribution Panel
Location for installation of Main Feeder Pillar cum timer Control Panel for Street Light & Highmast
SR NO | Equipment Name | Chainage | Qty | Remark
1 | Street Light & Highmast | 270 | 1 | Panel Rusted & Damaged
2 | Street Light & Highmast | 274.17 | 1 | Panel Rusted & Damaged
3 | Street Light & Highmast | 277.66 | 1 | Panel Rusted & Damaged
4 | Street Light & Highmast | 282.38 | 1 | Panel Rusted & Damaged
5 | Street Light & Highmast | 288.2 | 1 | Panel Rusted & Damaged
6 | Street Light | 289.12 | 1 | Panel Rusted & Damaged
7 | Street Light | 290.6 | 1 | Not Available
8 | Street Light | 314.64 | 1 | Not Available
9 | Street Light & Highmast | 315 | 1 | Panel Rusted & Damaged
10 | Street Light & Highmast | 334.25 | 1 | Panel Rusted & Damaged
11 | Street Light & Highmast | 336.65 | 1 | Panel Rusted & Damaged
12 | Street Light | 348.6 | 1 | Not Available
13 | Street Light & Highmast | 358.05 | 1 | Panel Rusted & Damaged
14 | Highmast | 361.6 | 1 | Panel Rusted & Damaged
15 | Street Light & Highmast | 363.65 | 1 | Panel Rusted & Damaged
16 | Highmast | 365.45 | 1 | Panel Rusted & Damaged
17 | Street Light & Highmast | 370.1 | 1 | Not Available
18 | LED STREET LIGHT | 370.7 | 1 | Not Available
19 | Highmast | 372.35 | 1 | Not Available
20 | HPSV STREET LIGHT | 377.35 | 1 | Not Available
21 | LED STREET LIGHT | 382.75 | 1 | Not Available
22 | HPSV STREET LIGHT | 383.65 | 1 | Not Available
23 | HPSV STREET LIGHT | 388.13 | 1 | Not Available
24 | HPSV STREET LIGHT | 392.47 | 1 | Not Available
25 | HPSV STREET LIGHT | 396.2 | 1 | Panel Rusted & Damaged
26 | HPSV STREET LIGHT | 396.2 | 1 | Panel Rusted & Damaged
27 | HPSV STREET LIGHT | 401.45 | 1 | Panel Rusted & Damaged
28 | LED STREET LIGHT | 403.4 | 1 | Not Available
29 | HPSV STREET LIGHT | 407.6 | 2 | Panel Rusted & Damaged
30 | LED STREET LIGHT | 413.9 | 1 | Not Available
31 | HPSV STREET LIGHT | 417.8 | 2 | Panel Rusted & Damaged
32 | HPSV STREET LIGHT | 418.75 | 2 | Panel Rusted & Damaged
Total |  |  | 35

## 2-Timer
(Annexure-42b)
TIMERS, CONTACTORS, MCB, MCCB
S. No. | Chainage |  | Side | Location | Highmast/ Street Light | Timer | Remark
1 | 262.9 | 263.15 | LHS | Truck Layby | Street Light | 1
2 | 266.52 | 266.52 | LHS | Shoulder | Highmast | 1 | Faridpur Toll Plaza
3 | 266.62 | 266.62 | RHS | Shoulder | Highmast | 1 | Faridpur Toll Plaza
4 | 266.72 | 266.72 | LHS | Shoulder | Highmast | 1 | Faridpur Toll Plaza
5 | 266.98 | 266.98 | LHS | Shoulder | Highmast | 1 | Faridpur Toll Plaza
6 | 266.98 | 266.98 | RHS | Shoulder | Highmast | 1 | Faridpur Toll Plaza
7 | 267.1 | 267.1 | LHS | Shoulder | Highmast | - | Faridpur Toll Plaza
8 | 267.1 | 267.1 | RHS | Shoulder | Highmast | - | Faridpur Toll Plaza
9 | 267.16 | 267.16 | RHS | Shoulder | Highmast | 1 | Faridpur Toll Plaza
10 | 267.29 | 267.29 | LHS | Shoulder | Highmast | 1 | Faridpur Toll Plaza
11 | 268.15 | 268.15 | RHS | Shoulder | Highmast | 1
12 | 269.7 | 270.35 | Median | MCW | Street Light | 1
13 | 270.1 | 270.1 | RHS | Shoulder | Highmast | -
14 | 277.3 | 278.1 | Median | MCW | Street Light | 1
15 | 277.77 | 277.77 | LHS | Shoulder | Highmast | 1
16 | 277.77 | 277.77 | RHS | Shoulder | Highmast | 1
17 | 282 | 282.8 | Median | MCW | Street Light | 2
18 | 282.38 | 282.38 | LHS | Shoulder | Highmast | 1
19 | 282.38 | 282.38 | RHS | Shoulder | Highmast | 1
20 | 287.85 | 288.65 | Median | MCW | Street Light | 2
21 | 288.9 | 289.5 | Median | MCW | Street Light | 2
22 | 295 | 295.73 | LHS | MCW | Street Light | 2
23 | 295 | 295.73 | RHS | MCW | Street Light | 2
24 | 295.37 | 295.37 | RHS | Shoulder | Highmast | 1
25 | 303.25 | 303.95 | Median | MCW | Street Light | 2
26 | 303.65 | 303.65 | RHS | Shoulder | Highmast | 1
27 | 305.05 | 305.9 | LHS | MCW | Street Light | 2
28 | 305.05 | 305.9 | RHS | MCW | Street Light | 2
29 | 305.41 | 305.41 | LHS | Shoulder | Highmast | 1
30 | 305.41 | 305.41 | RHS | Shoulder | Highmast | 1
31 | 306.15 | 306.3 | RHS | Truck Layby | Street Light | 1
32 | 315.35 | 316 | LHS | MCW | Street Light | 1
33 | 315.75 | 315.75 | LHS | Shoulder | Highmast | 1
34 | 315.75 | 315.75 | RHS | Shoulder | Highmast | -
35 | 317.42 | 317.42 | LHS | Shoulder | Highmast | 1
36 | 325.1 | 326 | LHS | MCW | Street Light | 2
37 | 325.1 | 326 | RHS | MCW | Street Light | 2
38 | 325.63 | 325.63 | LHS | Shoulder | Highmast | 1
39 | 325.63 | 325.63 | RHS | Shoulder | Highmast | 1
40 | 329.1 | 330 | LHS | MCW | Street Light | 2
41 | 329.1 | 330 | RHS | MCW | Street Light | 2
42 | 329.56 | 329.56 | LHS | Shoulder | Highmast | 1
43 | 329.56 | 329.56 | RHS | Shoulder | Highmast | 1
44 | 331.95 | 331.95 | RHS | Shoulder | Highmast | -
45 | 332.25 | 332.25 | LHS | Shoulder | Highmast | -
46 | 332.25 | 332.25 | RHS | Shoulder | Highmast | 1
47 | 336.6 | 336.6 | RHS | Shoulder | Highmast | 1
48 | 357.6 | 358.45 | Median | MCW | Street Light | 1
49 | 358.1 | 358.1 | LHS | Shoulder | Highmast | 1
50 | 358.1 | 358.1 | RHS | Shoulder | Highmast | 1
51 | 360.57 | 360.57 | RHS | Shoulder | Highmast | 1
52 | 361.6 | 361.6 | LHS | Shoulder | Highmast | 1
53 | 361.6 | 361.6 | RHS | Shoulder | Highmast | 1
54 | 363.4 | 363.95 | Median | MCW | Street Light | 1
55 | 365.45 | 365.45 | LHS | Shoulder | Highmast | 1
56 | 369.65 | 370.7 | Median | MCW | Street Light | 2
57 | 370.1 | 370.1 | RHS | Shoulder | Highmast | 1
58 | 371.75 | 371.75 | RHS | Shoulder | Highmast | - | Maigalganj Toll Plaza
59 | 371.82 | 371.82 | LHS | Shoulder | Highmast | - | Maigalganj Toll Plaza
60 | 372.02 | 372.02 | LHS | Shoulder | Highmast | - | Maigalganj Toll Plaza
61 | 372.35 | 372.35 | LHS | Shoulder | Highmast | 1 | Maigalganj Toll Plaza
62 | 372.35 | 372.35 | RHS | Shoulder | Highmast | 1 | Maigalganj Toll Plaza
63 | 374.08 | 374.08 | RHS | Shoulder | Highmast | -
64 | 376.8 | 378 | Median | MCW | Street Light | 2
65 | 383.2 | 384.2 | Median | MCW | Street Light | 2
66 | 383.65 | 383.65 | LHS | Shoulder | Highmast | 1
67 | 383.65 | 383.65 | RHS | Shoulder | Highmast | 1
68 | 387.8 | 388.6 | Median | MCW | Street Light | 2
69 | 388.13 | 388.13 | LHS | Shoulder | Highmast | -
70 | 391.9 | 393 | Median | MCW | Street Light | 2
71 | 395.55 | 395.55 | RHS | Shoulder | Highmast | 1
72 | 395.75 | 396.6 | LHS | MCW | Street Light | 1
73 | 395.75 | 396.6 | RHS | MCW | Street Light | 1
74 | 401.5 | 401.5 | RHS | Shoulder | Highmast | 1
75 | 402.6 | 404 | RHS | MCW | Street Light | 2
76 | 407.29 | 408 | LHS | MCW | Street Light | 2
77 | 407.35 | 408 | RHS | MCW | Street Light | 2
78 | 407.6 | 407.6 | LHS | Shoulder | Highmast | -
79 | 416.34 | 417.06 | LHS | MCW | Street Light | 1
80 | 416.34 | 417.07 | RHS | MCW | Street Light | 1
81 | 416.55 | 416.55 | LHS | Shoulder | Highmast | 1
82 | 417.35 | 419.3 | Median | MCW | Street Light | 4
83 | 417.8 | 417.8 | LHS | Shoulder | Highmast | 1
Total Sum | [5 empty] | 94
Spare | [5 empty] | 60
Note:- All necessary contactors, timers, MCBs, etc., have been replaced by the departmental team. The quantities specified in the BOQ are estimates; they will be considered for billing only if installed by the vendor based on actual site requirements during the execution of the work.

## 3-MCCB 100A
(Annexure-42b)
TIMERS, CONTACTORS, MCB, MCCB
S. No. | Chainage |  | Side | Location | Highmast/ Street Light | MCCB 100A | Remark
1 | 269.7 | 270.35 | Median | MCW | Street Light | 1
2 | 282.38 | 282.38 | LHS | Shoulder | Highmast | 1
3 | 282.38 | 282.38 | RHS | Shoulder | Highmast | 1
4 | 295 | 295.73 | LHS | MCW | Street Light | 1
5 | 295 | 295.73 | RHS | MCW | Street Light | 1
Total Sum | [5 empty] | 5
Spare
Note:- All necessary contactors, timers, MCBs, etc., have been replaced by the departmental team. The quantities specified in the BOQ are estimates; they will be considered for billing only if installed by the vendor based on actual site requirements during the execution of the work.

## 9- MCB 1 Pole
MCB 6A-25A 1 Pole
SR NO | Equipment Name | Chainage | Village Name | Description | Chainage |  |  | Total no of Pole | Total No of Fixture | MCB 6A-25A 1 Pole | Remark
[5 empty] | From | To | Length in Mtr
1 | LED STREET LIGHT | 263 | Kesharpur Truck Lay By | Truck Lay By | 262.9 | 263.15 | 250 | 8 | 8 | 8 |  | LED Street Light | 493
3 | Toll Plaza | 266.98 | Toll Plaza | Toll Plaza | 266.82 | 266.98 | 160 | 0 | 0 | 20 |  | HPSV STREET LIGHT | 310
6 | HPSV STREET LIGHT | 270.1 | Faridpur Bypass Bareilly | HPSV STREET LIGHT | 269.7 | 270.35 | 650 | 26 | 52 | 5 |  | Toll Plaza | 40
8 | HPSV STREET LIGHT | 274.17 | NEAR GURUDWARA FARIDPUR | HPSV STREET LIGHT | 273.7 | 274.45 | 750 | 28 | 56 | 5
9 | HPSV STREET LIGHT | 277.75 | Faridpur Bareilly | Highmast | 277.3 | 278.1 | 800 | 28 | 56 | 5
10 | HPSV STREET LIGHT | 282.38 | NEELAM VENEER, Tisuwa | HPSV STREET LIGHT | 282 | 282.8 | 800 | 29 | 58 | 5
11 | HPSV STREET LIGHT | 288.2 | Uchesiya Mod Fatehganj Purbi Near Gupta Restourent | HPSV STREET LIGHT | 287.85 | 288.65 | 800 | 29 | 58 | 5
12 | HPSV STREET LIGHT | 289.12 | Fatehganj Purbi | HPSV STREET LIGHT | 288.9 | 289.5 | 600 | 22 | 44 | 5
13 | LED STREET LIGHT | 290.6 | Shalpur Navdia ROB | HPSV STREET LIGHT | 290.05 | 291.35 | 1300 | 167 | 167 | 167
14 | HPSV STREET LIGHT | 295.37 | Katara Chauraha LHS | HPSV STREET LIGHT | 295 | 295.73 | 730 | 30 | 60 | 5
15 | HPSV STREET LIGHT | 295.37 | Katara Chauraha RHS | HPSV STREET LIGHT | 295 | 295.73 | 730 | 30 | 60 | 30
16 | HPSV STREET LIGHT | 303.65 | Mansoorpur Tilhar Cut | HPSV STREET LIGHT | 303.25 | 303.95 | 700 | 26 | 52 | 5
17 | HPSV STREET LIGHT | 305.44 | Tilahar LHS | HPSV STREET LIGHT | 305.05 | 305.9 | 850 | 37 | 74 | 5
18 | HPSV STREET LIGHT | 305.41 | Tilahar RHS | HPSV STREET LIGHT | 305.05 | 305.9 | 850 | 37 | 74 | 5
19 | LED STREET LIGHT | 306.1 | Tilhar City Rd Truck Lay By | Truck Lay By | 306.15 | 306.3 | 150 | 8 | 8 | 8
21 | LED STREET LIGHT | 314.64 | Street Light | HPSV STREET LIGHT | 314.3 | 314.9 | 600 | 36 | 72 | 72
22 | HPSV STREET LIGHT | 315.75 | Banthara | HPSV STREET LIGHT | 315.35 | 316 | 650 | 58 | 116 | 5
24 | HPSV STREET LIGHT | 325.58 | Bareilly Mod LHS | HPSV STREET LIGHT | 325.1 | 326 | 900 | 32 | 64 | 10
25 | HPSV STREET LIGHT | 325.63 | Bareilly Mod RHS | HPSV STREET LIGHT | 325.1 | 326 | 900 | 30 | 60 | 15
26 | HPSV STREET LIGHT | 329.56 | Near BHARAT DHABA BRIDGE LHS | HPSV STREET LIGHT | 329.1 | 330 | 900 | 34 | 68 | 10
27 | HPSV STREET LIGHT | 329.56 | Roza Bypass RHS | HPSV STREET LIGHT | 329.1 | 330 | 900 | 35 | 70 | 10
29 | HPSV STREET LIGHT | 331.95 | NEAR DOON SCHOOL LHS, Ahmadpur Niwazpur | HPSV STREET LIGHT | 331.6 | 332.05 | 450 | 17 | 34 | 10
30 | HPSV STREET LIGHT | 331.95 | NEAR DOON SCHOOL RHS Ahmadpur Niwazpur | HPSV STREET LIGHT | 331.6 | 332.05 | 450 | 16 | 32 | 10
31 | HPSV STREET LIGHT | 332.25 | Honda Colony, Roza - 2 LHS Mandi Marg | HPSV STREET LIGHT | 332.05 | 332.5 | 450 | 16 | 32 | 10
32 | HPSV STREET LIGHT | 332.25 | Kuda Plant, Roza -1 RHS Mandi Marg | HPSV STREET LIGHT | 332.05 | 332.5 | 450 | 17 | 34 | 10
33 | HPSV STREET LIGHT | 334.25 | ROB RAILWAY CROSSING, LHS | HPSV STREET LIGHT | 333.7 | 334.9 | 1200 | 70 | 140 | 40
35 | HPSV STREET LIGHT | 336.65 | Jamuhi, Shajahanpur Rd | HPSV STREET LIGHT | 336.3 | 337.1 | 800 | 66 | 132 | 10
36 | LED STREET LIGHT | 348.6 | Truck Lay By | Truck Lay By | 348.45 | 348.7 | 250 | 16 | 16 | 16
38 | HPSV STREET LIGHT | 358.05 | Barkheriya Jat | HPSV STREET LIGHT | 357.6 | 358.45 | 850 | 33 | 66 | 5
41 | HPSV STREET LIGHT | 363.65 | Highmast RHS | HPSV STREET LIGHT | 363.4 | 363.95 | 550 | 21 | 42 | 5
43 | HPSV STREET LIGHT | 370.1 | Chhapartala | HPSV STREET LIGHT | 369.65 | 370.7 | 1050 | 43 | 86 | 5
44 | LED STREET LIGHT | 370.7 | Truck Lay By | Truck Lay By | 370.7 | 371.7 | 1000 | 8 | 8 | 8
46 | Toll Plaza | 372.1 | Toll Plaza Maigalganj | Toll Plaza | 372.02 | 372.18 | 160 | 0 | 0 | 20
49 | HPSV STREET LIGHT | 377.4 | Aurangabad / Maigalganj Bypass | HPSV STREET LIGHT | 376.8 | 378 | 1200 | 45 | 90 | 15
51 | LED STREET LIGHT | 382.75 | Truck Lay By | Truck Lay By | 382.45 | 382.7 | 250 | 8 | 8 | 8
52 | HPSV STREET LIGHT | 383.65 | Neri, Maholi | HPSV STREET LIGHT | 383.2 | 384.2 | 1000 | 42 | 84 | 5
53 | HPSV STREET LIGHT | 388.13 | Bhudiya PO Kachuri, Sitapur | HPSV STREET LIGHT | 387.8 | 388.6 | 800 | 32 | 64 | 5
54 | HPSV STREET LIGHT | 392.47 | Badagaon Maholi | HPSV STREET LIGHT | 391.9 | 393 | 1100 | 41 | 82 | 5
56 | HPSV STREET LIGHT | 396.2 | Maholi LHS | HPSV STREET LIGHT | 395.75 | 396.6 | 850 | 32 | 64 | 5
57 | HPSV STREET LIGHT | 396.2 | Maholi RHS | HPSV STREET LIGHT | 395.75 | 396.6 | 850 | 32 | 64 | 10
58 | HPSV STREET LIGHT | 401.45 | RICHHAI CHAURAHA | HPSV STREET LIGHT | 401.1 | 402 | 900 | 35 | 70 | 5
59 | LED STREET LIGHT | 403.4 | Hempur ROB RHS | LED STREET LIGHT | 402.6 | 404 | 1400 | 59 | 118 | 59
60 | LED STREET LIGHT | 403.65 | Hempur ROB LHS | LED STREET LIGHT | 402.6 | 404 | 1400 | 59 | 118 | 59
62 | HPSV STREET LIGHT | 407.57 | Katili Bridge LHS | HPSV STREET LIGHT | 407.29 | 408 | 710 | 27 | 54 | 5
63 | HPSV STREET LIGHT | 407 | PAPER MILL BRIDGE II, KATILI RHS | HPSV STREET LIGHT | 407.29 | 408 | 710 | 28 | 56 | 5
65 | LED STREET LIGHT | 413.85 | Naveen Chowk, OVER BRIDGE | LED STREET LIGHT | 413.83 | 413.83 | 0 | 30 | 60 | 30
67 | LED STREET LIGHT | 416.75 | ROTI GODAM KANWAKHEDA | LED STREET LIGHT | 416.34 | 417.06 | 720 | 58 | 116 | 58
68 | HPSV STREET LIGHT | 417.8 | Bahuguda Chauraha Bridge | LED STREET LIGHT | 417.35 | 418.05 | 700 | 26 | 52 | 5
70 | HPSV STREET LIGHT | 418.7 | kamta sariya-1 | HPSV STREET LIGHT | 418.05 | 418.75 | 700 | 26 | 52 | 5
71 | HPSV STREET LIGHT | 418.7 | kamta sariya-2 | HPSV STREET LIGHT | 418.75 | 419.35 | 600 | 28 | 56 | 5
Spare | [9 empty] | 1157
Total SUM | [9 empty] | 2000

## 12& 17 - 10Sqmm AL Cable
10.0 Sq.mm 3 core & 4 core XLPE Aluminium Armoured Cable
Sr No | Equipment | Backup | Power Source | Connection Load Requirement | ATMS Location | Location of Existing Connection | Distance from Existing Connection | Distance From Existing Connection under 100 mtr | Distance B/W 100 - 450 mtr for cable laying | Distance above the 450 mtr for new connection considering | Cable will be laid by Agency +Extra ROW to Median | 10.0 Sq.mm XLPE Aluminium Armoured Cable | Existing Connection taken for the Equipment | Remark
3 | TMCS | 6hrs | Solar with Raw Power | 1KVA | 263.2 | 263 | 0.2 |  | 0.2 |  | 0.1 | 0.1 | LED Street Light | The cable laying work for ATMS equipment falls under the scope of the ATMS agency. The fixed distance under the agency’s scope has not yet been finalized. As per the email received from the agency and the instructions from our ATMS team, a length of 100 meters has been considered as fixed under the agency’s scope. Based on this, the average cable length has been calculated for the balance length, which will fall under the scope of NHIT, while at the same locations, 100 meters of cable length will remain under the agency’s scope.
9 | TMCS | 6hrs | Solar with Raw Power | 2KVA | 268 | 268.15 | 0.15 |  | 0.15 |  | 0.1 | 0.05 | Highmast
20 | TMCS | 6hrs | Solar with Raw Power | 1KVA | 274 | 274.17 | 0.17 |  | 0.17 |  | 0.1 | 0.07 | HPSV Street Light
24 | TMCS | 6hrs | Solar with Raw Power | 1KVA | 278 | 277.75 | 0.25 |  | 0.25 |  | 0.1 | 0.15 | HPSV Street Light
30 | TMCS | 6hrs | Solar with Raw Power | 1KVA | 282 | 282.38 | 0.38 |  | 0.38 |  | 0.1 | 0.28 | HPSV Street Light
34 | TMCS | 24hrs | Only Solar power | NA | 286 | 286.3 | 0.3 |  | 0.3 |  | 0 | 0.3 | VMS
35 | L VMS | 24hrs | Solar with Raw Power | 1KVA | 286.65 | 286.3 | 0.35 |  | 0.35 |  | 0.1 | 0.25 | VMS
37 | TMCS | 6hrs | Solar with Raw Power | 1KVA | 288 | 288.2 | 0.2 |  | 0.2 |  | 0.1 | 0.1 | HPSV Street Light
38 | TMCS | 6hrs | Solar with Raw Power | 1KVA | 289 | 289.12 | 0.12 |  | 0.12 |  | 0.1 | 0.02 | HPSV Street Light
41 | TMCS | 6hrs | Solar with Raw Power | 1KVA | 290 | 289.73 | 0.27 |  | 0.27 |  | 0.1 | 0.17 | New Proposed VADS
42 | TMCS | 6hrs | Solar with Raw Power | 1KVA | 291 | 290.6 | 0.4 |  | 0.4 |  | 0.1 | 0.3 | LED Street Light
49 | L VMS | 24hrs | Solar with Raw Power | 1KVA | 294.55 | 294.4 | 0.15 |  | 0.15 |  | 0.1 | 0.05 | VIDS/PTZ Camera
50 | TMCS | 6hrs | Solar with Raw Power | 1KVA | 295 | 295.37 | 0.37 |  | 0.37 |  | 0.1 | 0.27 | HPSV Street Light
60 | TMCS | 6hrs | Solar with Raw Power | 1KVA | 303.2 | 303.65 | 0.45 |  | 0.45 |  | 0.1 | 0.35 | HPSV Street Light
61 | TMCS | 6hrs | Solar with Raw Power | 1KVA | 304 | 303.65 | 0.35 |  | 0.35 |  | 0.1 | 0.25 | HPSV Street Light
62 | TMCS | 6hrs | Solar with Raw Power | 1KVA | 305 | 305.44 | 0.44 |  | 0.44 |  | 0.1 | 0.34 | HPSV Street Light
67 | TMCS | 24hrs | Only Solar power | NA | 309 | 309.2 | 0.2 |  | 0.2 |  | 0 | 0.2 | VMS
68 | VASD | 6hrs | Solar with Raw Power | 2kva | 309.4 | 309.2 | 0.2 |  | 0.2 |  | 0.1 | 0.1 | VMS
69 | VASD | 6hrs | Solar with Raw Power | 2kva | 309.41 | 309.2 | 0.21 |  | 0.21 |  | 0.1 | 0.11 | VMS
79 | TMCS | 24hrs | Only Solar power | NA | 317 | 317.42 | 0.42 |  | 0.42 |  | 0.1 | 0.32 | highmast Connection Pending
80 | L VMS | 24hrs | Solar with Raw Power | 1KVA | 317.18 | 317.42 | 0.24 |  | 0.24 |  | 0.1 | 0.14 | highmast Connection Pending
91 | TMCS | 24hrs | Only Solar power | NA | 326 | 325.58 | 0.42 |  | 0.42 |  | 0.1 | 0.32 | HPSV Street Light
98 | VASD | 6hrs | Solar with Raw Power | 2kva | 330.25 | 330.6 | 0.35 |  | 0.35 |  | 0.1 | 0.25 | VMS
99 | VASD | 6hrs | Solar with Raw Power |  | 330.26 |  | -330.26
101 | TMCS | 6hrs | Solar with Raw Power | 1KVA | 331 | 330.6 | 0.4 |  | 0.4 |  | 0.1 | 0.3 | VMS
105 | TMCS | 6hrs | Solar with Raw Power | 1KVA | 334 | 334.25 | 0.25 |  | 0.25 |  | 0.1 | 0.15 | HPSV Street Light
106 | TMCS | 6hrs | Solar with Raw Power | 1KVA | 335 | 334.85 | 0.15 |  | 0.15 |  | 0.1 | 0.05 | HPSV Street Light
108 | TMCS | 24hrs | Only Solar power | NA | 337 | 336.65 | 0.35 |  | 0.35 |  | 0 | 0.35 | HPSV Street Light
134 | TMCS | 24hrs | Only Solar power | NA | 356 | 356.35 | 0.35 |  | 0.35 |  | 0.1 | 0.25 | Highmast
140 | TMCS | 6hrs | Solar with Raw Power | 1KVA | 359 | 358.75 | 0.25 |  | 0.25 |  | 0.1 | 0.15 | VMS connection Pending
143 | VIDES | 6hrs | Solar with Raw Power | 2KVA | 360.35 | 360.57 | 0.22 |  | 0.22 |  | 0.1 | 0.12 | Highmast
144 | VIDES | 6hrs | Solar with Raw Power |  | 360.45 | 360.57 | 0.12 |  | 0.12 |  | 0.1 | 0.02 | Highmast
145 | TMCS | 6hrs | Solar with Raw Power | 2KVA | 361 | 360.57 | 0.43 |  | 0.43 |  | 0.1 | 0.33 | Highmast
146 | L VMS | 24hrs | Solar with Raw Power |  | 361.2 | 361.63 | 0.43 |  | 0.43 |  | 0.1 | 0.33 | Highmast
147 | TMCS | 6hrs | Solar with Raw Power | 1KVA | 362 | 361.63 | 0.37 |  | 0.37 |  | 0.1 | 0.27 | Highmast
149 | TMCS | 6hrs | Solar with Raw Power | 1KVA | 364 | 363.65 | 0.35 |  | 0.35 |  | 0.1 | 0.25 | HPSV Street Light
150 | TMCS | 6hrs | Solar with Raw Power | 1KVA | 365 | 365.45 | 0.45 |  | 0.45 |  | 0.1 | 0.35 | Highmast
155 | VASD | 6hrs | Solar with Raw Power | 2kva | 369.3 | 369.65 | 0.35 |  | 0.35 |  | 0.1 | 0.25 | HPSV Street Light
156 | VASD | 6hrs | Solar with Raw Power |  | 369.35 | 369.65 | 0.3 |  | 0.3 |  | 0.1 | 0.2 | HPSV Street Light
159 | TMCS | 6hrs | Solar with Raw Power | 1KVA | 371 | 370.7 | 0.3 |  | 0.3 |  | 0.1 | 0.2 | LED Street Light connection Pending
162 | L VMS | 24hrs | Solar with Raw Power | 1KVA | 373.85 | 374.08 | 0.23 |  | 0.23 |  | 0.1 | 0.13 | Highmast
163 | VIDES | 6hrs | Solar with Raw Power | 2KVA | 373.92 | 374.08 | 0.16 |  | 0.16 |  | 0.1 | 0.06 | Highmast
168 | TMCS | 24hrs | Only Solar power | NA | 377 | 377.4 | 0.4 |  | 0.4 |  | 0.1 | 0.3 | HPSV Street Light
184 | VASD | 6hrs | Solar with Raw Power | 2kva | 387.69 | 388.13 | 0.44 |  | 0.44 |  | 0.1 | 0.34 | HPSV Street Light
185 | VASD | 6hrs | Solar with Raw Power |  | 387.7 | 388.13 | 0.43 |  | 0.43 |  | 0.1 | 0.33 | HPSV Street Light
186 | TMCS | 24hrs | Only Solar power | NA | 388 | 388.13 | 0.13 |  | 0.13 |  | 0 | 0.13 | HPSV Street Light
188 | TMCS | 24hrs | Only Solar power | NA | 389 | 389.12 | 0.12 |  | 0.12 |  | 0.1 | 0.02 | ATMS
198 | TMCS | 24hrs | Only Solar power | NA | 396 | 396.2 | 0.2 |  | 0.2 |  | 0 | 0.2 | Highmast
199 | L VMS | 24hrs | Solar with Raw Power | 1KVA | 396.65 | 396.2 | 0.45 |  | 0.45 |  | 0.1 | 0.35 | HPSV Street Light
204 | TMCS | 6hrs | Solar with Raw Power | 1KVA | 401 | 401.45 | 0.45 |  | 0.45 |  | 0.1 | 0.35 | HPSV Street Light
206 | TMCS | 24hrs | Only Solar power | NA | 403 | 403.4 | 0.4 |  | 0.4 |  | 0.1 | 0.3 | LED Street Light
222 | VIDES | 6hrs | Solar with Raw Power | 2KVA | 412.27 | 412.45 | 0.18 |  | 0.18 |  | 0.1 | 0.08 | Highmast
223 | VIDES | 6hrs | Solar with Raw Power |  | 412.3 | 412.45 | 0.15 |  | 0.15 |  | 0.1 | 0.05 | Highmast
226 | L VMS | 24hrs | Solar with Raw Power | 1KVA | 413.55 | 413.85 | 0.3 |  | 0.3 |  | 0.1 | 0.2 | Highmast
230 | TMCS | 6hrs | Solar with Raw Power | 1KVA | 417 | 416.75 | 0.25 |  | 0.25 |  | 0.1 | 0.15 | NA
231 | TMCS | 6hrs | Solar with Raw Power | 1KVA | 418 | 417.8 | 0.2 |  | 0.2 |  | 0.1 | 0.1 | NA
232 | TMCS | 6hrs | Solar with Raw Power |  | 419 | 419.15 | 0.15 |  | 0.15 |  | 0.1 | 0.05 | NA
233 | L VMS | 24hrs | Only Solar power |  | 419 | 419.15 | 0.15 |  | 0.15 |  | 0.1 | 0.05 | HPSV Street Light
234 | M-VMS | 6hrs | Solar with Raw Power | 5KVA | 419.15 | 419.4 | 0.25 |  | 0.25 |  | 0.1 | 0.15 | VMS
Total Length in Mtr | [7 empty] | 0 | 16700 | 0 | 5300 | 11400
20 % Exta Lenght (if the agency is not able to provide cable above 100 Mtr) | [11 empty] | 2280
Total Cable for ATMS supply | [11 empty] | 13680
For Both Toll, Trucklay rest room, toilet room & admin Building from main electrical Panel | [11 empty] | 1320
Total Length of required cable in Mtr | [11 empty] | 15000

## Timer & Contactor
(Annexure-42b)
TIMERS, CONTACTORS, MCB, MCCB
S. No. | Chainage |  | Side | Location | Highmast/ Street Light | MCB 1 Pole | MCCB 100A | MCB 63A, 4 Pole | Contactor | Timer | Motor | Chain | Remark
1 | 262.9 | 263.15 | LHS | Truck Layby | Street Light |  | - |  | - | 1
2 | 266.52 | 266.52 | LHS | Shoulder | Highmast |  |  | - | 1 | 1 | - | - | Faridpur Toll Plaza
3 | 266.62 | 266.62 | RHS | Shoulder | Highmast |  |  | - | 1 | 1 | - | - | Faridpur Toll Plaza
4 | 266.72 | 266.72 | LHS | Shoulder | Highmast |  |  | 1 | 1 | 1 | - | - | Faridpur Toll Plaza
5 | 266.98 | 266.98 | LHS | Shoulder | Highmast |  |  | - | 1 | 1 | - | - | Faridpur Toll Plaza
6 | 266.98 | 266.98 | RHS | Shoulder | Highmast |  |  | - | 1 | 1 | - | - | Faridpur Toll Plaza
7 | 267.1 | 267.1 | LHS | Shoulder | Highmast |  |  | - | 1 | - | - | - | Faridpur Toll Plaza
8 | 267.1 | 267.1 | RHS | Shoulder | Highmast |  |  | - | 1 | - | - | - | Faridpur Toll Plaza
9 | 267.16 | 267.16 | RHS | Shoulder | Highmast |  |  | - | 1 | 1 | - | - | Faridpur Toll Plaza
10 | 267.29 | 267.29 | LHS | Shoulder | Highmast |  |  | - | 1 | 1 | 1 | 1 | Faridpur Toll Plaza
11 | 268.15 | 268.15 | RHS | Shoulder | Highmast |  |  | - | 1 | 1 | - | -
12 | 269.7 | 270.35 | Median | MCW | Street Light |  | 1 | - | 1 | 1
13 | 270.1 | 270.1 | RHS | Shoulder | Highmast |  |  | - | - | - | 1 | 1
14 | 277.3 | 278.1 | Median | MCW | Street Light |  | - | - | 1 | 1
15 | 277.77 | 277.77 | LHS | Shoulder | Highmast |  |  | - | - | 1 | - | -
16 | 277.77 | 277.77 | RHS | Shoulder | Highmast |  |  | - | - | 1 | - | -
17 | 282 | 282.8 | Median | MCW | Street Light |  | - | - | 2 | 2
18 | 282.38 | 282.38 | LHS | Shoulder | Highmast |  | 1 | - | 1 | 1 | - | -
19 | 282.38 | 282.38 | RHS | Shoulder | Highmast |  | 1 | - | 1 | 1 | - | -
20 | 287.85 | 288.65 | Median | MCW | Street Light |  | - | - | 2 | 2
21 | 288.9 | 289.5 | Median | MCW | Street Light |  | - | - | 2 | 2
22 | 295 | 295.73 | LHS | MCW | Street Light |  | 1 | 3 | 2 | 2
23 | 295 | 295.73 | RHS | MCW | Street Light |  | 1 | 3 | 2 | 2
24 | 295.37 | 295.37 | RHS | Shoulder | Highmast |  |  | - | 1 | 1 | - | -
25 | 303.25 | 303.95 | Median | MCW | Street Light |  | - | - | 2 | 2
26 | 303.65 | 303.65 | RHS | Shoulder | Highmast |  |  | - | 1 | 1 | 1 | 1
27 | 305.05 | 305.9 | LHS | MCW | Street Light |  | - | - | 2 | 2
28 | 305.05 | 305.9 | RHS | MCW | Street Light |  | - | - | 2 | 2
29 | 305.41 | 305.41 | LHS | Shoulder | Highmast |  |  | - | 1 | 1 | - | -
30 | 305.41 | 305.41 | RHS | Shoulder | Highmast |  |  | - | 1 | 1 | - | -
31 | 306.15 | 306.3 | RHS | Truck Layby | Street Light |  | - | - | - | 1
32 | 315.35 | 316 | LHS | MCW | Street Light |  | - | - | 1 | 1
33 | 315.75 | 315.75 | LHS | Shoulder | Highmast |  |  | - | 1 | 1 | 1 | 1
34 | 315.75 | 315.75 | RHS | Shoulder | Highmast |  |  | - | - | - | 1 | 1
35 | 317.42 | 317.42 | LHS | Shoulder | Highmast |  |  | - | 1 | 1 | - | -
36 | 325.1 | 326 | LHS | MCW | Street Light |  | - | - | 2 | 2
37 | 325.1 | 326 | RHS | MCW | Street Light |  | - | - | 2 | 2
38 | 325.63 | 325.63 | LHS | Shoulder | Highmast |  |  | - | 1 | 1 | 1 | 1
39 | 325.63 | 325.63 | RHS | Shoulder | Highmast |  |  | - | 1 | 1 | - | -
40 | 329.1 | 330 | LHS | MCW | Street Light |  | - | - | 2 | 2
41 | 329.1 | 330 | RHS | MCW | Street Light |  | - | - | 2 | 2
42 | 329.56 | 329.56 | LHS | Shoulder | Highmast |  |  | - | 1 | 1 | - | -
43 | 329.56 | 329.56 | RHS | Shoulder | Highmast |  |  | - | 1 | 1 | - | -
44 | 331.95 | 331.95 | RHS | Shoulder | Highmast |  |  | - | - | - | 1 | 1
45 | 332.25 | 332.25 | LHS | Shoulder | Highmast |  |  | - | - | - | 1 | 1
46 | 332.25 | 332.25 | RHS | Shoulder | Highmast |  |  | - | 1 | 1 | 1 | 1
47 | 336.6 | 336.6 | RHS | Shoulder | Highmast |  |  | - | 1 | 1 | - | -
48 | 357.6 | 358.45 | Median | MCW | Street Light |  |  |  | 1 | 1
49 | 358.1 | 358.1 | LHS | Shoulder | Highmast |  |  | - | 1 | 1 | - | -
50 | 358.1 | 358.1 | RHS | Shoulder | Highmast |  |  | - | 1 | 1 | - | -
51 | 360.57 | 360.57 | RHS | Shoulder | Highmast |  |  | 1 | 1 | 1 | - | -
52 | 361.6 | 361.6 | LHS | Shoulder | Highmast |  |  | - | 1 | 1 | - | -
53 | 361.6 | 361.6 | RHS | Shoulder | Highmast |  |  | 1 | 1 | 1 | - | -
54 | 363.4 | 363.95 | Median | MCW | Street Light |  | - | - | 1 | 1
55 | 365.45 | 365.45 | LHS | Shoulder | Highmast |  |  | - | 1 | 1 | - | -
56 | 369.65 | 370.7 | Median | MCW | Street Light |  | - | - | 2 | 2
57 | 370.1 | 370.1 | RHS | Shoulder | Highmast |  |  | - | 1 | 1 | - | -
58 | 371.75 | 371.75 | RHS | Shoulder | Highmast |  |  | - | - | - | 1 | 1 | Maigalganj Toll Plaza
59 | 371.82 | 371.82 | LHS | Shoulder | Highmast |  |  | - | - | - | 1 | 1 | Maigalganj Toll Plaza
60 | 372.02 | 372.02 | LHS | Shoulder | Highmast |  |  | - | - | - | - | 1 | Maigalganj Toll Plaza
61 | 372.35 | 372.35 | LHS | Shoulder | Highmast |  |  | - | 1 | 1 | - | 1 | Maigalganj Toll Plaza
62 | 372.35 | 372.35 | RHS | Shoulder | Highmast |  |  | - | 1 | 1 | - | - | Maigalganj Toll Plaza
63 | 374.08 | 374.08 | RHS | Shoulder | Highmast |  |  | - | - | - | - | 1
64 | 376.8 | 378 | Median | MCW | Street Light |  | - | - | 2 | 2
65 | 383.2 | 384.2 | Median | MCW | Street Light |  | - | - | 2 | 2
66 | 383.65 | 383.65 | LHS | Shoulder | Highmast |  |  | - | 1 | 1 | - | -
67 | 383.65 | 383.65 | RHS | Shoulder | Highmast |  |  | - | 1 | 1
68 | 387.8 | 388.6 | Median | MCW | Street Light |  | - | - | 2 | 2
69 | 388.13 | 388.13 | LHS | Shoulder | Highmast |  |  | - | - | - | - | 1
70 | 391.9 | 393 | Median | MCW | Street Light |  | - | - | 2 | 2
71 | 395.55 | 395.55 | RHS | Shoulder | Highmast |  |  | - | 1 | 1 | - | -
72 | 395.75 | 396.6 | LHS | MCW | Street Light |  | - | - | 1 | 1
73 | 395.75 | 396.6 | RHS | MCW | Street Light |  | - | - | 1 | 1
74 | 401.5 | 401.5 | RHS | Shoulder | Highmast |  |  | 1 | 1 | 1
75 | 402.6 | 404 | RHS | MCW | Street Light |  | - | - | 2 | 2
76 | 407.29 | 408 | LHS | MCW | Street Light |  | - | - | 2 | 2
77 | 407.35 | 408 | RHS | MCW | Street Light |  | - | - | 2 | 2
78 | 407.6 | 407.6 | LHS | Shoulder | Highmast |  |  | - | - | - | 1 | 1
79 | 416.34 | 417.06 | LHS | MCW | Street Light |  | - | - | 1 | 1
80 | 416.34 | 417.07 | RHS | MCW | Street Light |  | - | - | 1 | 1
81 | 416.55 | 416.55 | LHS | Shoulder | Highmast |  |  | - | - | 1 | - | -
82 | 417.35 | 419.3 | Median | MCW | Street Light |  | - | - | 4 | 4
83 | 417.8 | 417.8 | LHS | Shoulder | Highmast |  |  | - | 1 | 1 | - | -
Major requirement of one Pole MCB required for all existing 699 No's LED light fixture (263.000, 290.600, 306.100, 314.640, 348.600, 370.700, 382.750, 403.400, 403.650, 413.850, 416.750) & othar all location where HPSV Light available & at toll plaza if required | [5 empty] | 2000
Total Sum | [5 empty] | 2000 | 5 | 10 | 91 | 94 | 12 | 16
Spare
Note:- All necessary contactors, timers, MCBs, etc., have been replaced by the departmental team. The quantities specified in the BOQ are estimates; they will be considered for billing only if installed by the vendor based on actual site requirements during the execution of the work.

## 19- 63 mm DWC Pipe
10.0 Sq.mm 3 core & 4 core XLPE Aluminium Armoured Cable
Sr No | Equipment | Backup | Power Source | Connection Load Requirement | ATMS Location | Location of Existing Connection | Distance from Existing Connection | 10.0 Sq.mm XLPE Aluminium Armoured Cable | Existing Connection taken for the Equipment | Remark
3 | TMCS | 6hrs | Solar with Raw Power | 1KVA | 263.2 | 263 | 0.2 | 0.1 | LED Street Light | The cable laying work for ATMS equipment falls under the scope of the ATMS agency. The fixed distance under the agency’s scope has not yet been finalized. As per the email received from the agency and the instructions from our ATMS team, a length of 100 meters has been considered as fixed under the agency’s scope. Based on this, the average cable length has been calculated for the balance length, which will fall under the scope of NHIT, while at the same locations, 100 meters of cable length will remain under the agency’s scope.
9 | TMCS | 6hrs | Solar with Raw Power | 2KVA | 268 | 268.15 | 0.15 | 0.05 | Highmast
20 | TMCS | 6hrs | Solar with Raw Power | 1KVA | 274 | 274.17 | 0.17 | 0.07 | HPSV Street Light
24 | TMCS | 6hrs | Solar with Raw Power | 1KVA | 278 | 277.75 | 0.25 | 0.15 | HPSV Street Light
30 | TMCS | 6hrs | Solar with Raw Power | 1KVA | 282 | 282.38 | 0.38 | 0.28 | HPSV Street Light
34 | TMCS | 24hrs | Only Solar power | NA | 286 | 286.3 | 0.3 | 0.3 | VMS
35 | L VMS | 24hrs | Solar with Raw Power | 1KVA | 286.65 | 286.3 | 0.35 | 0.25 | VMS
37 | TMCS | 6hrs | Solar with Raw Power | 1KVA | 288 | 288.2 | 0.2 | 0.1 | HPSV Street Light
38 | TMCS | 6hrs | Solar with Raw Power | 1KVA | 289 | 289.12 | 0.12 | 0.02 | HPSV Street Light
41 | TMCS | 6hrs | Solar with Raw Power | 1KVA | 290 | 289.73 | 0.27 | 0.17 | New Proposed VADS
42 | TMCS | 6hrs | Solar with Raw Power | 1KVA | 291 | 290.6 | 0.4 | 0.3 | LED Street Light
49 | L VMS | 24hrs | Solar with Raw Power | 1KVA | 294.55 | 294.4 | 0.15 | 0.05 | VIDS/PTZ Camera
50 | TMCS | 6hrs | Solar with Raw Power | 1KVA | 295 | 295.37 | 0.37 | 0.27 | HPSV Street Light
60 | TMCS | 6hrs | Solar with Raw Power | 1KVA | 303.2 | 303.65 | 0.45 | 0.35 | HPSV Street Light
61 | TMCS | 6hrs | Solar with Raw Power | 1KVA | 304 | 303.65 | 0.35 | 0.25 | HPSV Street Light
62 | TMCS | 6hrs | Solar with Raw Power | 1KVA | 305 | 305.44 | 0.44 | 0.34 | HPSV Street Light
67 | TMCS | 24hrs | Only Solar power | NA | 309 | 309.2 | 0.2 | 0.2 | VMS
68 | VASD | 6hrs | Solar with Raw Power | 2kva | 309.4 | 309.2 | 0.2 | 0.1 | VMS
69 | VASD | 6hrs | Solar with Raw Power | 2kva | 309.41 | 309.2 | 0.21 | 0.11 | VMS
79 | TMCS | 24hrs | Only Solar power | NA | 317 | 317.42 | 0.42 | 0.32 | highmast Connection Pending
80 | L VMS | 24hrs | Solar with Raw Power | 1KVA | 317.18 | 317.42 | 0.24 | 0.14 | highmast Connection Pending
91 | TMCS | 24hrs | Only Solar power | NA | 326 | 325.58 | 0.42 | 0.32 | HPSV Street Light
98 | VASD | 6hrs | Solar with Raw Power | 2kva | 330.25 | 330.6 | 0.35 | 0.25 | VMS
99 | VASD | 6hrs | Solar with Raw Power |  | 330.26 |  | -330.26
101 | TMCS | 6hrs | Solar with Raw Power | 1KVA | 331 | 330.6 | 0.4 | 0.3 | VMS
105 | TMCS | 6hrs | Solar with Raw Power | 1KVA | 334 | 334.25 | 0.25 | 0.15 | HPSV Street Light
106 | TMCS | 6hrs | Solar with Raw Power | 1KVA | 335 | 334.85 | 0.15 | 0.05 | HPSV Street Light
108 | TMCS | 24hrs | Only Solar power | NA | 337 | 336.65 | 0.35 | 0.35 | HPSV Street Light
134 | TMCS | 24hrs | Only Solar power | NA | 356 | 356.35 | 0.35 | 0.25 | Highmast
140 | TMCS | 6hrs | Solar with Raw Power | 1KVA | 359 | 358.75 | 0.25 | 0.15 | VMS connection Pending
143 | VIDES | 6hrs | Solar with Raw Power | 2KVA | 360.35 | 360.57 | 0.22 | 0.12 | Highmast
144 | VIDES | 6hrs | Solar with Raw Power |  | 360.45 | 360.57 | 0.12 | 0.02 | Highmast
145 | TMCS | 6hrs | Solar with Raw Power | 2KVA | 361 | 360.57 | 0.43 | 0.33 | Highmast
146 | L VMS | 24hrs | Solar with Raw Power |  | 361.2 | 361.63 | 0.43 | 0.33 | Highmast
147 | TMCS | 6hrs | Solar with Raw Power | 1KVA | 362 | 361.63 | 0.37 | 0.27 | Highmast
149 | TMCS | 6hrs | Solar with Raw Power | 1KVA | 364 | 363.65 | 0.35 | 0.25 | HPSV Street Light
150 | TMCS | 6hrs | Solar with Raw Power | 1KVA | 365 | 365.45 | 0.45 | 0.35 | Highmast
155 | VASD | 6hrs | Solar with Raw Power | 2kva | 369.3 | 369.65 | 0.35 | 0.25 | HPSV Street Light
156 | VASD | 6hrs | Solar with Raw Power |  | 369.35 | 369.65 | 0.3 | 0.2 | HPSV Street Light
159 | TMCS | 6hrs | Solar with Raw Power | 1KVA | 371 | 370.7 | 0.3 | 0.2 | LED Street Light connection Pending
162 | L VMS | 24hrs | Solar with Raw Power | 1KVA | 373.85 | 374.08 | 0.23 | 0.13 | Highmast
163 | VIDES | 6hrs | Solar with Raw Power | 2KVA | 373.92 | 374.08 | 0.16 | 0.06 | Highmast
168 | TMCS | 24hrs | Only Solar power | NA | 377 | 377.4 | 0.4 | 0.3 | HPSV Street Light
184 | VASD | 6hrs | Solar with Raw Power | 2kva | 387.69 | 388.13 | 0.44 | 0.34 | HPSV Street Light
185 | VASD | 6hrs | Solar with Raw Power |  | 387.7 | 388.13 | 0.43 | 0.33 | HPSV Street Light
186 | TMCS | 24hrs | Only Solar power | NA | 388 | 388.13 | 0.13 | 0.13 | HPSV Street Light
188 | TMCS | 24hrs | Only Solar power | NA | 389 | 389.12 | 0.12 | 0.02 | ATMS
198 | TMCS | 24hrs | Only Solar power | NA | 396 | 396.2 | 0.2 | 0.2 | Highmast
199 | L VMS | 24hrs | Solar with Raw Power | 1KVA | 396.65 | 396.2 | 0.45 | 0.35 | HPSV Street Light
204 | TMCS | 6hrs | Solar with Raw Power | 1KVA | 401 | 401.45 | 0.45 | 0.35 | HPSV Street Light
206 | TMCS | 24hrs | Only Solar power | NA | 403 | 403.4 | 0.4 | 0.3 | LED Street Light
222 | VIDES | 6hrs | Solar with Raw Power | 2KVA | 412.27 | 412.45 | 0.18 | 0.08 | Highmast
223 | VIDES | 6hrs | Solar with Raw Power |  | 412.3 | 412.45 | 0.15 | 0.05 | Highmast
226 | L VMS | 24hrs | Solar with Raw Power | 1KVA | 413.55 | 413.85 | 0.3 | 0.2 | Highmast
230 | TMCS | 6hrs | Solar with Raw Power | 1KVA | 417 | 416.75 | 0.25 | 0.15 | NA
231 | TMCS | 6hrs | Solar with Raw Power | 1KVA | 418 | 417.8 | 0.2 | 0.1 | NA
232 | TMCS | 6hrs | Solar with Raw Power |  | 419 | 419.15 | 0.15 | 0.05 | NA
233 | L VMS | 24hrs | Only Solar power |  | 419 | 419.15 | 0.15 | 0.05 | HPSV Street Light
234 | M-VMS | 6hrs | Solar with Raw Power | 5KVA | 419.15 | 419.4 | 0.25 | 0.15 | VMS
Total Length in Mtr | [7 empty] | 11400
20 % Exta Length (if the agency is not able to provide cable above 100 Mtr) | [7 empty] | 2280
Total Cable for ATMS supply | [7 empty] | 13680
For Both Toll, Trucklay rest room, toilet room & admin Building from main electrical Panel | [7 empty] | 6320
Total Length of required cable in Mtr | [7 empty] | 20000

## 19- 63mm DWC Site & Toll
Details for Laying of DWC HDPE Pipe for highway street Light & Toll Plaza
SR NO | Equipment Name | Chainage | Village Name | Description | Chainage |  | DWC HDPE Pipe 63 mm | Remark
[5 empty] | From | To
1 | LED STREET LIGHT | 263 | Kesharpur Truck Lay By | Truck Lay By | 262.9 | 263.15 | 150
2 | Highmast | 266.62 | Faridpur Toll Highmast A1 Side | Highmast | 266.62 | 266.82 | 100
3 | Toll Plaza | 266.98 | Toll Plaza | Toll Plaza | 266.82 | 266.98 | 300
4 | Highmast | 267.2 | Faridpur Toll Toll Highmast A2 Side | Highmast | 267.1 | 267.29 | 20
5 | HPSV STREET LIGHT | 270.1 | Faridpur Bypass Bareilly | HPSV STREET LIGHT | 269.7 | 270.35 | 120
6 | Highmast | 272.5 | Faridpur Tiraha | Highmast | 272.52 | 272.52 | 120
7 | HPSV STREET LIGHT | 274.17 | NEAR GURUDWARA FARIDPUR | HPSV STREET LIGHT | 273.7 | 274.45 | 120
8 | HPSV STREET LIGHT | 277.75 | Faridpur Bareilly | Highmast | 277.3 | 278.1 | 120
9 | HPSV STREET LIGHT | 282.38 | NEELAM VENEER, Tisuwa | HPSV STREET LIGHT | 282 | 282.8 | 120
10 | HPSV STREET LIGHT | 288.2 | Uchesiya Mod Fatehganj Purbi Near Gupta Restourent | HPSV STREET LIGHT | 287.85 | 288.65 | 100
11 | HPSV STREET LIGHT | 289.12 | Fatehganj Purbi | HPSV STREET LIGHT | 288.9 | 289.5 | 200
12 | HPSV STREET LIGHT | 295.37 | Katara Chauraha LHS | HPSV STREET LIGHT | 295 | 295.73 | 40
13 | HPSV STREET LIGHT | 295.37 | Katara Chauraha RHS | HPSV STREET LIGHT | 295 | 295.73 | 40
14 | HPSV STREET LIGHT | 303.65 | Mansoorpur Tilhar Cut | HPSV STREET LIGHT | 303.25 | 303.95 | 150
15 | HPSV STREET LIGHT | 305.44 | Tilahar LHS | HPSV STREET LIGHT | 305.05 | 305.9 | 80
16 | HPSV STREET LIGHT | 305.41 | Tilahar RHS | HPSV STREET LIGHT | 305.05 | 305.9 | 80
17 | LED STREET LIGHT | 306.1 | Tilhar City Rd Truck Lay By | Truck Lay By | 306.15 | 306.3 | 120
18 | LED STREET LIGHT | 314.64 | Street Light | HPSV STREET LIGHT | 314.3 | 314.9 | 160
19 | HPSV STREET LIGHT | 315.75 | Banthara | HPSV STREET LIGHT | 315.35 | 316 | 100
20 | HPSV STREET LIGHT | 325.58 | Bareilly Mod LHS | HPSV STREET LIGHT | 325.1 | 326 | 100
21 | HPSV STREET LIGHT | 325.63 | Bareilly Mod RHS | HPSV STREET LIGHT |  |  | 100
22 | HPSV STREET LIGHT | 329.56 | Near BHARAT DHABA BRIDGE LHS | HPSV STREET LIGHT | 329.1 | 330 | 100
23 | HPSV STREET LIGHT | 329.56 | Roza Bypass RHS | HPSV STREET LIGHT | 329.1 | 330 | 80
24 | HPSV STREET LIGHT | 334.25 | ROB RAILWAY CROSSING, LHS | Highmast | 334.25 | 334.65 | 300 | From Transfor to VUP
25 | LED STREET LIGHT | 348.6 | Truck Lay By | Truck Lay By | 348.45 | 348.7 | 510
26 | HPSV STREET LIGHT | 358.05 | Barkheriya Jat | HPSV STREET LIGHT | 357.6 | 358.45 | 150
27 | HPSV STREET LIGHT | 363.65 | Highmast RHS | HPSV STREET LIGHT | 363.4 | 363.95 | 150
28 | HPSV STREET LIGHT | 370.1 | Chhapartala | HPSV STREET LIGHT | 369.65 | 370.7 | 180
29 | LED STREET LIGHT | 370.7 | Truck Lay By | Truck Lay By | 370.7 | 371.7 | 270
30 | Toll Plaza | 372.1 | Toll Plaza Maigalganj | Toll Plaza | 372.02 | 372.18 | 300
31 | HPSV STREET LIGHT | 377.4 | Aurangabad / Maigalganj Bypass | HPSV STREET LIGHT | 376.8 | 378 | 150
32 | LED STREET LIGHT | 382.75 | Truck Lay By | Truck Lay By | 382.45 | 382.7 | 150
33 | HPSV STREET LIGHT | 383.65 | Neri, Maholi | HPSV STREET LIGHT | 383.2 | 384.2 | 150
34 | HPSV STREET LIGHT | 388.13 | Bhudiya PO Kachuri, Sitapur | HPSV STREET LIGHT | 387.8 | 388.6 | 150
35 | HPSV STREET LIGHT | 392.47 | Badagaon Maholi | HPSV STREET LIGHT | 391.9 | 393 | 150
36 | HPSV STREET LIGHT | 401.45 | RICHHAI CHAURAHA | HPSV STREET LIGHT | 401.1 | 402 | 150
37 | LED STREET LIGHT | 403.4 | Hempur ROB RHS | LED STREET LIGHT | 402.6 | 404 | 150
38 | LED STREET LIGHT | 403.65 | Hempur ROB LHS | LED STREET LIGHT | 402.6 | 404 | 150
39 | LED STREET LIGHT | 413.85 | Naveen Chowk, OVER BRIDGE | LED STREET LIGHT | 413.83 | 413.83 | 150
40 | LED STREET LIGHT | 416.75 | ROTI GODAM KANWAKHEDA | LED STREET LIGHT | 416.34 | 417.06 | 130
41 | HPSV STREET LIGHT | 417.8 | Bahuguda Chauraha Bridge | LED STREET LIGHT | 417.35 | 418.05 | 120
42 | HPSV STREET LIGHT | 418.7 | kamta sariya-1 | HPSV STREET LIGHT | 418.05 | 418.75 | 120
43 | HPSV STREET LIGHT | 418.7 | kamta sariya-2 | HPSV STREET LIGHT | 418.75 | 419.35 | 120
Total SUM | [6 empty] | 6320

## 20- HDPE pipe 100 mm
DWC HDPE PIPE 100 mm Dia (OD-100 mm & ID-90 mm nominal)
SR NO | Equipment Name | Chainage | Qty | Remark
1 | Street Light & Highmast | 270 | 45 | It has been considered to lay a 100 mm dia. HDPE pipe from the ROW Main Feeder Pillar to the median of the VUP for the street lighting cable.
2 | Street Light & Highmast | 274.17 | 45
3 | Street Light & Highmast | 277.66 | 45
4 | Street Light & Highmast | 282.38 | 45
5 | Street Light & Highmast | 288.2 | 45
6 | Street Light | 289.12 | 45
7 | Street Light | 290.6 | 45
8 | Street Light | 314.64 | 45
9 | Street Light & Highmast | 315 | 45
10 | Street Light & Highmast | 334.25 | 100
11 | Street Light & Highmast | 336.65 | 50
12 | Street Light | 348.6 | 45
13 | Street Light & Highmast | 358.05 | 45
14 | Highmast | 361.6 | 45
15 | Street Light & Highmast | 363.65 | 45
16 | Highmast | 365.45 | 45
17 | Street Light & Highmast | 370.1 | 45
18 | LED STREET LIGHT | 370.7 | 45
19 | Highmast | 372.35 | 45
20 | HPSV STREET LIGHT | 377.35 | 45
21 | LED STREET LIGHT | 382.75 | 45
22 | HPSV STREET LIGHT | 383.65 | 45
23 | HPSV STREET LIGHT | 388.13 | 45
24 | HPSV STREET LIGHT | 392.47 | 45
25 | HPSV STREET LIGHT | 396.2 | 45
26 | HPSV STREET LIGHT | 396.2 | 45
27 | HPSV STREET LIGHT | 401.45 | 45
28 | LED STREET LIGHT | 403.4 | 45
29 | HPSV STREET LIGHT | 407.6 | 45
30 | LED STREET LIGHT | 413.9 | 45
31 | HPSV STREET LIGHT | 417.8 | 45
32 | HPSV STREET LIGHT | 418.75 | 45
Total |  |  | 1500

## 13-18 AL Cable
Location for Providing & Laying of Aluminium Armoured Cable for Highway street Light, ATMS & Toll plaza Cable Renovation
SR NO | Equipment Name | Chainage | Village Name | Description | Chainage |  |  | Total no of Pole | Total No of Fixture | Al. Armoured cable 4X16 Sq , mm for pole to Cable replacement | Al. Armoured cable 4X25 Sq , mm from Feeder Pillar to First Pole & Cable renovation at Toll Plaza | Al. Armoured cable 4X35 Sq , mm from Transformer to Fedder Pillar or as per site requirement(For Heavy Load) | Al. Armoured cable 3.5X50 Sq , mm from Transformer to Fedder Pillar | Al. Armoured cable 3.5X70 Sq , mm from Transformer to Fedder Pillar | Remark
[5 empty] | From | To | Length in Mtr
1 | LED STREET LIGHT | 263 | Kesharpur Truck Lay By | Truck Lay By | 262.9 | 263.15 | 250 | 8 | 8 | 270 | 70 |  |  |  | Over head cable installed at side for street light & Required to Replace the existing overhead unarmoured cable with a suitably rated underground cable due to inadequate load-carrying capacity.
2 | Highmast | 266.62 | Faridpur Toll Highmast A1 Side | Highmast | 266.62 | 266.82 | 200 | 0 | 0 | 150 |  | 30 |  |  | In Place of damaged cable replacement
3 | Toll Plaza | 266.98 | Toll Plaza | Toll Plaza | 266.82 | 266.98 | 160 | 0 | 0 |  | 5000 |  |  |  | Cable required at the toll plaza for renovation work, as per the connected load and site conditions.
4 | Highmast | 267.2 | Faridpur Toll Toll Highmast A2 Side | Highmast | 267.1 | 267.29 | 190 | 0 | 0 | 20 |  | 30 |  |  | In Place of damaged cable replacement
5 | Highmast | 268.15 | Gausganj Sarai near Khandelwal Oils | Highmast | 268.15 | 268.15 | 0 | 0 | 0 |  |  | 30
6 | HPSV STREET LIGHT | 270.1 | Faridpur Bypass Bareilly | HPSV STREET LIGHT | 269.7 | 270.35 | 650 | 26 | 52 | 120 |  |  |  | 30 | In Place of damaged cable replacement
7 | Highmast | 272.5 | Faridpur Tiraha | Highmast | 272.52 | 272.52 | 0 | 0 | 0 | 120 |  | 30 |  |  | In Place of damaged cable replacement
8 | HPSV STREET LIGHT | 274.17 | NEAR GURUDWARA FARIDPUR | HPSV STREET LIGHT | 273.7 | 274.45 | 750 | 28 | 56 | 120 |  |  |  | 30 | In Place of damaged cable replacement
9 | HPSV STREET LIGHT | 277.75 | Faridpur Bareilly | Highmast | 277.3 | 278.1 | 800 | 28 | 56 | 120 |  |  | 30 | 30 | In Place of damaged cable replacement
10 | HPSV STREET LIGHT | 282.38 | NEELAM VENEER, Tisuwa | HPSV STREET LIGHT | 282 | 282.8 | 800 | 29 | 58 | 120 | 180 |  | 30 |  | In Place of damaged cable replacement
11 | HPSV STREET LIGHT | 288.2 | Uchesiya Mod Fatehganj Purbi Near Gupta Restourent | HPSV STREET LIGHT | 287.85 | 288.65 | 800 | 29 | 58 | 120 | 60 |  | 30 |  | In Place of damaged cable replacement
12 | HPSV STREET LIGHT | 289.12 | Fatehganj Purbi | HPSV STREET LIGHT | 288.9 | 289.5 | 600 | 22 | 44 | 240 | 60 |  | 30 |  | In Place of damaged cable replacement
13 | LED STREET LIGHT | 290.6 | Shalpur Navdia ROB | HPSV STREET LIGHT | 290.05 | 291.35 | 1300 | 167 | 167 | 5040 | 260 |  |  | 30 | The existing unarmoured cables installed between the poles are incapable of carrying the electrical load of the street lights.
14 | HPSV STREET LIGHT | 295.37 | Katara Chauraha LHS | HPSV STREET LIGHT | 295 | 295.73 | 730 | 30 | 60 | 30 | 60 |  | 130 |  | In Place of damaged cable replacement
15 | HPSV STREET LIGHT | 295.37 | Katara Chauraha RHS | HPSV STREET LIGHT | 295 | 295.73 | 730 | 30 | 60 | 30 | 60 |  | 150 |  | In Place of damaged cable replacement
16 | HPSV STREET LIGHT | 303.65 | Mansoorpur Tilhar Cut | HPSV STREET LIGHT | 303.25 | 303.95 | 700 | 26 | 52 | 210 |  |  | 30
17 | HPSV STREET LIGHT | 305.44 | Tilahar LHS | HPSV STREET LIGHT | 305.05 | 305.9 | 850 | 37 | 74 | 60 | 60 | 100 |  | 30
18 | HPSV STREET LIGHT | 305.41 | Tilahar RHS | HPSV STREET LIGHT | 305.05 | 305.9 | 850 | 37 | 74 | 60 | 60 | 120 |  | 30
19 | LED STREET LIGHT | 306.1 | Tilhar City Rd Truck Lay By | Truck Lay By | 306.15 | 306.3 | 150 | 8 | 8 | 270 | 70 |  |  |  | Over head cable installed at side for street light & Required to Replace the existing overhead unarmoured cable with a suitably rated underground cable due to inadequate load-carrying capacity.
20 | Highmast | 307 |  | Highmast | 307 | 307 | 0 | 0 | 0
21 | LED STREET LIGHT | 314.64 | Street Light | HPSV STREET LIGHT | 314.3 | 314.9 | 600 | 36 | 72 | 2190 | 180 |  |  |  | The existing unarmoured cables installed between the poles are incapable of carrying the electrical load of the street lights.
22 | HPSV STREET LIGHT | 315.75 | Banthara | HPSV STREET LIGHT | 315.35 | 316 | 650 | 58 | 116 | 60 | 140 |  | 50
23 | Highmast | 317.42 | HIGHMAST LHS | Highmast | 317.42 | 317.42 | 0 | 0 | 0 |  | 30 |  |  |  | For replacement of service cable from the transformer to to the feeder pillar to prevent overheating.
24 | HPSV STREET LIGHT | 325.58 | Bareilly Mod LHS | HPSV STREET LIGHT | 325.1 | 326 | 900 | 32 | 64 | 60 |  | 100 |  | 30
25 | HPSV STREET LIGHT | 325.63 | Bareilly Mod RHS | HPSV STREET LIGHT |  |  |  | 30 | 60 | 60 |  | 100 |  | 30
26 | HPSV STREET LIGHT | 329.56 | Near BHARAT DHABA BRIDGE LHS | HPSV STREET LIGHT | 329.1 | 330 | 900 | 34 | 68 | 60 |  | 100 |  | 30
27 | HPSV STREET LIGHT | 329.56 | Roza Bypass RHS | HPSV STREET LIGHT | 329.1 | 330 | 900 | 35 | 70 | 60 |  | 100 |  | 30
28 | Highmast | 331.7 | Roza Bypass RHS | Highmast | 331.7 | 331.7 | 0 | 0 | 0 |  | 60 |  |  |  | For replacement of service cable from the transformer to to the feeder pillar to prevent overheating.
29 | HPSV STREET LIGHT | 331.95 | NEAR DOON SCHOOL LHS, Ahmadpur Niwazpur | HPSV STREET LIGHT | 331.6 | 332.05 | 450 | 17 | 34 |  |  | 20 | 30
30 | HPSV STREET LIGHT | 331.95 | NEAR DOON SCHOOL RHS Ahmadpur Niwazpur | HPSV STREET LIGHT | 331.6 | 332.05 | 450 | 16 | 32 |  |  | 20 | 30
31 | HPSV STREET LIGHT | 332.25 | Honda Colony, Roza - 2 LHS Mandi Marg | HPSV STREET LIGHT | 332.05 | 332.5 | 450 | 16 | 32 |  |  | 20 | 30
32 | HPSV STREET LIGHT | 332.25 | Kuda Plant, Roza -1 RHS Mandi Marg | HPSV STREET LIGHT | 332.05 | 332.5 | 450 | 17 | 34
33 | HPSV STREET LIGHT | 334.25 | ROB RAILWAY CROSSING, LHS | HPSV STREET LIGHT | 333.7 | 334.9 | 1200 | 70 | 140
34 | Highmast | 334.9 | ROB RAILWAY CROSSING, LHS | Highmast | 334.9 | 334.9 | 0 | 0 | 0 |  | 30 |  |  |  | For replacement of service cable from the transformer to to the feeder pillar to prevent overheating.
35 | HPSV STREET LIGHT | 336.65 | Jamuhi, Shajahanpur Rd | HPSV STREET LIGHT | 336.3 | 337.1 | 800 | 66 | 132 |  |  | 220 |  | 30
36 | LED STREET LIGHT | 348.6 | Truck Lay By | Truck Lay By | 348.45 | 348.7 | 250 | 16 | 16 | 510 | 200 | 170 |  |  | Over head cable installed at side for street light & Required to Replace the existing overhead unarmoured cable with a suitably rated underground cable due to inadequate load-carrying capacity.
37 | Highmast | 356.35 | PANAI CHAURAHA | Highmast | 356.35 | 356.35 | 0 | 0 | 0 |  | 50 | 30 |  |  | For replacement of service cable from the transformer to to the feeder pillar to prevent overheating.
38 | HPSV STREET LIGHT | 358.05 | Barkheriya Jat | HPSV STREET LIGHT | 357.6 | 358.45 | 850 | 33 | 66 | 90 |  |  |  | 30
39 | Highmast | 360.57 | Udaypur, JB Ganj | Highmast | 360.57 | 360.57 | 0 | 0 | 0 |  | 30 |  |  |  | For replacement of service cable from the transformer to to the feeder pillar to prevent overheating.
40 | Highmast | 361.63 | Highmast BHS | Highmast | 361.6 | 361.6 | 0 | 0 | 0 |  |  | 30
41 | HPSV STREET LIGHT | 363.65 | Highmast RHS | HPSV STREET LIGHT | 363.4 | 363.95 | 550 | 21 | 42 | 90 |  |  |  | 30
42 | Highmast | 365.45 | Pihani Mod | Highmast | 365.45 | 365.45 | 0 | 0 | 0 |  |  | 30
43 | HPSV STREET LIGHT | 370.1 | Chhapartala | HPSV STREET LIGHT | 369.65 | 370.7 | 1050 | 43 | 86 | 180 | 190 |  |  | 30
44 | LED STREET LIGHT | 370.7 | Truck Lay By | Truck Lay By | 370.7 | 371.7 | 1000 | 8 | 8 | 270 | 70 |  |  |  | Over head cable installed at side for street light & Required to Replace the existing overhead unarmoured cable with a suitably rated underground cable due to inadequate load-carrying capacity.
45 | Highmast | 372.1 | Aurangabad Khiri | Highmast | 371.75 | 371.92 | 170 | 0 | 0 |  |  |  |  | 30
46 | Toll Plaza | 372.1 | Toll Plaza Maigalganj | Toll Plaza | 372.02 | 372.18 | 160 | 0 | 0 |  | 5000 |  |  |  | Cable required at the toll plaza for renovation work, as per the connected load and site conditions.
47 | Highmast | 372.35 | Maigalganj Toll, Highmast Sitapur Side | Highmast | 372.26 | 372.48 | 220 | 0 | 0 |  | 120 |  |  | 30 | For replacement of service cable from the transformer to to the feeder pillar to prevent overheating.
48 | Highmast | 374.08 | Rahjaniya, Maigalganj | Highmast | 374.08 | 374.08 | 0 | 0 | 0
49 | HPSV STREET LIGHT | 377.4 | Aurangabad / Maigalganj Bypass | HPSV STREET LIGHT | 376.8 | 378 | 1200 | 45 | 90 | 120 | 170 |  |  | 30
50 | Highmast | 380.05 | Highmast RHS | Highmast | 380.05 | 380.05 | 0 | 0 | 0 |  | 60 |  |  |  | For replacement of service cable from the transformer to to the feeder pillar to prevent overheating.
51 | LED STREET LIGHT | 382.75 | Truck Lay By | Truck Lay By | 382.45 | 382.7 | 250 | 8 | 8 | 270 | 70 |  |  |  | Over head cable installed at side for street light & Required to Replace the existing overhead unarmoured cable with a suitably rated underground cable due to inadequate load-carrying capacity.
52 | HPSV STREET LIGHT | 383.65 | Neri, Maholi | HPSV STREET LIGHT | 383.2 | 384.2 | 1000 | 42 | 84 | 120 |  |  |  | 30 | In Place of damaged cable replacement
53 | HPSV STREET LIGHT | 388.13 | Bhudiya PO Kachuri, Sitapur | HPSV STREET LIGHT | 387.8 | 388.6 | 800 | 32 | 64 | 120 |  |  |  | 30 | In Place of damaged cable replacement
54 | HPSV STREET LIGHT | 392.47 | Badagaon Maholi | HPSV STREET LIGHT | 391.9 | 393 | 1100 | 41 | 82 | 120 |  |  | 30 |  | In Place of damaged cable replacement
55 | Highmast | 395.55 | Maholi, Sitapur | Highmast | 395 | 395 | 0 | 0 | 0
56 | HPSV STREET LIGHT | 396.2 | Maholi LHS | HPSV STREET LIGHT | 395.75 | 396.6 | 850 | 32 | 64 |  |  |  | 30
57 | HPSV STREET LIGHT | 396.2 | Maholi RHS | HPSV STREET LIGHT | 395.75 | 396.6 | 850 | 32 | 64 |  |  |  | 30
58 | HPSV STREET LIGHT | 401.45 | RICHHAI CHAURAHA | HPSV STREET LIGHT | 401.1 | 402 | 900 | 35 | 70 | 120 | 200 |  |  | 30 | In Place of damaged cable replacement
59 | LED STREET LIGHT | 403.4 | Hempur ROB RHS | LED STREET LIGHT | 402.6 | 404 | 1400 | 59 | 118 | 3570 | 170 |  |  | 30 | The existing unarmoured cables installed between the poles are incapable of carrying the electrical load of the street lights.
60 | LED STREET LIGHT | 403.65 | Hempur ROB LHS | LED STREET LIGHT | 402.6 | 404 | 1400 | 59 | 118 | 3570 | 140 |  |  | 30 | The existing unarmoured cables installed between the poles are incapable of carrying the electrical load of the street lights.
61 | Highmast | 403.57 | Hempur Highmast | Highmast | 403.57 | 403.57 | 0 | 0 | 0
62 | HPSV STREET LIGHT | 407.57 | Katili Bridge LHS | HPSV STREET LIGHT | 407.29 | 408 | 710 | 27 | 54 |  | 100 |  |  | 30 | In Place of damaged cable replacement
63 | HPSV STREET LIGHT | 407 | PAPER MILL BRIDGE II, KATILI RHS | HPSV STREET LIGHT | 407.29 | 408 | 710 | 28 | 56 |  | 120 |  |  | 30 | In Place of damaged cable replacement
64 | Highmast | 412.45 | Kashiram Colony, Sitapur | Highmast | 412.45 | 412.45 | 0 | 0 | 0 |  | 30 |  |  |  | For replacement of service cable from the transformer to to the feeder pillar to prevent overheating.
65 | LED STREET LIGHT | 413.85 | Naveen Chowk, OVER BRIDGE | LED STREET LIGHT | 413.83 | 413.83 | 0 | 30 | 60 | 1830 | 140 | 30 |  |  | The existing unarmoured cables installed between the poles are incapable of carrying the electrical load of the street lights.
66 | Highmast | 413.9 | Naveen Chowk Highmast | Highmast | 413.83 | 413.83 | 0 | 0 | 0 |  | 30 |  |  |  | For replacement of service cable from the transformer to to the feeder pillar to prevent overheating.
67 | LED STREET LIGHT | 416.75 | ROTI GODAM KANWAKHEDA | LED STREET LIGHT | 416.34 | 417.06 | 720 | 58 | 116 | 3510 | 200 |  |  | 30 | The existing unarmoured cables installed between the poles are incapable of carrying the electrical load of the street lights.
68 | HPSV STREET LIGHT | 417.8 | Bahuguda Chauraha Bridge | LED STREET LIGHT | 417.35 | 418.05 | 700 | 26 | 52 | 120 |  |  |  | 30 | In Place of damaged cable replacement
69 | Highmast | 417.8 | Lal Kurti Road, Sitapur | LED STREET LIGHT | 417.8 | 417.8 | 0 | 0 | 0 | 120 | 30 | 30 |  |  | For replacement of service cable from the transformer to to the feeder pillar to prevent overheating.
70 | HPSV STREET LIGHT | 418.7 | kamta sariya-1 | HPSV STREET LIGHT | 418.05 | 418.75 | 700 | 26 | 52 | 120 |  |  |  | 30 | In Place of damaged cable replacement
71 | HPSV STREET LIGHT | 418.7 | kamta sariya-2 | HPSV STREET LIGHT | 418.75 | 419.35 | 600 | 28 | 56 | 120 |  |  |  | 30 | In Place of damaged cable replacement
Spare | [9 empty] | 440 | 6500 | 660 | 340 | 160
Total SUM | [9 empty] | 25000 | 20000 | 2000 | 1000 | 1000

## 63 mm DWC Pipe for ATMS
Details for Laying of DWC HDPE Pipe for ATMS supply, Toll Electrical
Sr No | Equipment | Backup | Power Source | ATMS Location | Location of Existing Connection | DWC HDPE Pipe 63 mm in Mtr | Existing Connection taken for the Equipment | Status | Remark
M/O HDD Location
1 | TMCS | 6hrs | Solar with Raw Power | 263.2 | 263 | 100 | LED Street Light | Cable Provide | The cable laying work for ATMS equipment falls under the scope of the ATMS agency. The fixed distance under the agency’s scope has not yet been finalized. As per the email received from the agency and the instructions from our ATMS team, a length of 100 meters has been considered as fixed under the agency’s scope. Based on this, the average cable length has been calculated for the balance length, which will fall under the scope of NHIT, while at the same locations, 100 meters of cable length will remain under the agency’s scope.
2 | TMCS | 6hrs | Solar with Raw Power | 268 | 268.15 | 50 | Highmast | Cable Provide |  | 268.13
3 | TMCS | 6hrs | Solar with Raw Power | 274 | 274.17 | 70 | HPSV Street Light | Cable Provide
4 | TMCS | 6hrs | Solar with Raw Power | 278 | 277.75 | 150 | HPSV Street Light | Cable Provide
5 | TMCS | 6hrs | Solar with Raw Power | 282 | 282.38 | 280 | HPSV Street Light | Cable Provide
6 | TMCS | 24hrs | Only Solar power | 286 | 286.3 | 300 | VMS | Cable Provide
7 | L VMS | 24hrs | Solar with Raw Power | 286.65 | 286.3 | 250 | VMS | Cable Provide
8 | TMCS | 6hrs | Solar with Raw Power | 288 | 288.2 | 100 | HPSV Street Light | Cable Provide
9 | TMCS | 6hrs | Solar with Raw Power | 289 | 289.12 | 20 | HPSV Street Light | Cable Provide
10 | TMCS | 6hrs | Solar with Raw Power | 290 | 289.73 | 170 | New Proposed VADS | Cable Provide
11 | TMCS | 6hrs | Solar with Raw Power | 291 | 290.6 | 300 | LED Street Light | Cable Provide
12 | L VMS | 24hrs | Solar with Raw Power | 294.55 | 294.4 | 50 | VIDS/PTZ Camera | Cable Provide
13 | TMCS | 6hrs | Solar with Raw Power | 295 | 295.37 | 270 | HPSV Street Light | Cable Provide
14 | TMCS | 6hrs | Solar with Raw Power | 303.2 | 303.65 | 350 | HPSV Street Light | Cable Provide
15 | TMCS | 6hrs | Solar with Raw Power | 304 | 303.65 | 250 | HPSV Street Light | Cable Provide
16 | TMCS | 6hrs | Solar with Raw Power | 305 | 305.44 | 340 | HPSV Street Light | Cable Provide
17 | TMCS | 24hrs | Only Solar power | 309 | 309.2 | 200 | VMS | OK
18 | VASD | 6hrs | Solar with Raw Power | 309.4 | 309.2 | 100 | VMS | Cable Provide
19 | VASD | 6hrs | Solar with Raw Power | 309.41 | 309.2 | 110 | VMS | Cable Provide
20 | TMCS | 24hrs | Only Solar power | 317 | 317.42 | 320 | Camera Pending | Cable Provide
21 | L VMS | 24hrs | Solar with Raw Power | 317.18 | 317.42 | 140 | highmast Connection Pending | Cable Provide |  | 317.43
23 | VASD | 6hrs | Solar with Raw Power | 330.25 | 330.6 | 250 | VMS | Cable Provide |  | 330.4
24 | VASD | 6hrs | Solar with Raw Power | 330.26 |  | 0
25 | TMCS | 6hrs | Solar with Raw Power | 331 | 330.6 | 300 | VMS | Cable Provide
26 | TMCS | 6hrs | Solar with Raw Power | 334 | 334.25 | 150 | HPSV Street Light | Cable Provide
27 | TMCS | 6hrs | Solar with Raw Power | 335 | 334.85 | 50 | HPSV Street Light | Cable Provide
30 | TMCS | 6hrs | Solar with Raw Power | 359 | 358.75 | 150 | VMS connection Pending
31 | VIDES | 6hrs | Solar with Raw Power | 360.35 | 360.57 | 120 | Highmast | Cable Provide
32 | VIDES | 6hrs | Solar with Raw Power | 360.45 | 360.57 | 20 | Highmast | Cable Provide |  | 360.41
33 | TMCS | 6hrs | Solar with Raw Power | 361 | 360.57 | 330 | Highmast | Cable Provide |  | 360.45
34 | L VMS | 24hrs | Solar with Raw Power | 361.2 | 361.63 | 330 | Highmast | Cable Provide
35 | TMCS | 6hrs | Solar with Raw Power | 362 | 361.63 | 270 | Highmast | Cable Provide
36 | TMCS | 6hrs | Solar with Raw Power | 364 | 363.65 | 250 | HPSV Street Light | Cable Provide
37 | TMCS | 6hrs | Solar with Raw Power | 365 | 365.45 | 350 | Highmast | Cable Provide
38 | VASD | 6hrs | Solar with Raw Power | 369.3 | 369.65 | 250 | HPSV Street Light | Cable Provide
39 | VASD | 6hrs | Solar with Raw Power | 369.35 | 369.65 | 200 | HPSV Street Light | Cable Provide
40 | TMCS | 6hrs | Solar with Raw Power | 371 | 370.7 | 200 | LED Street Light connection Pending | Cable Provide |  | 370.8
41 | L VMS | 24hrs | Solar with Raw Power | 373.85 | 374.08 | 130 | Highmast | Cable Provide
42 | VIDES | 6hrs | Solar with Raw Power | 373.92 | 374.08 | 60 | Highmast | Cable Provide |  | 373.95
44 | VASD | 6hrs | Solar with Raw Power | 387.69 | 388.13 | 340 | HPSV Street Light | Cable Provide |  | 387.1
45 | VASD | 6hrs | Solar with Raw Power | 387.7 | 388.13 | 330 | HPSV Street Light
49 | L VMS | 24hrs | Solar with Raw Power | 396.65 | 396.2 | 350 | HPSV Street Light | Cable Provide
50 | TMCS | 6hrs | Solar with Raw Power | 401 | 401.45 | 350 | HPSV Street Light | Cable Provide
52 | VIDES | 6hrs | Solar with Raw Power | 412.27 | 412.45 | 80 | Highmast | Cable Provide |  | 412.27
53 | VIDES | 6hrs | Solar with Raw Power | 412.3 | 412.45 | 50 | Highmast | Cable Provide
54 | L VMS | 24hrs | Solar with Raw Power | 413.55 | 413.85 | 200 | Highmast | Cable Provide
55 | TMCS | 6hrs | Solar with Raw Power | 417 | 416.75 | 150 | NA | Cable Provide
56 | TMCS | 6hrs | Solar with Raw Power | 418 | 417.8 | 100 | NA | Cable Provide
57 | TMCS | 6hrs | Solar with Raw Power | 419 | 419.15 | 50 | NA | Cable Provide
58 | L VMS | 24hrs | Only Solar power | 419 | 419.15 | 50 | HPSV Street Light | Cable Provide
59 | M-VMS | 6hrs | Solar with Raw Power | 419.15 | 419.4 | 150 | VMS
Total Length in Mtr | [5 empty] | 9530
20 % Exta Lenght (if the agency is not able to provide cable above 100 Mtr) | [5 empty] | 1906
Total length for Laying of DWC HDPE Pipe for highway street Light & Toll Plaza | [5 empty] | 6320
spare if any require at any Location | [5 empty] | 1094
Total Sum | [5 empty] | 18850

## HDD with 100mm Pipe at Toll
HDD Work With 100 mm Dia PN6-8 grade HDPE Pipe for Toll plaza cable renovation work
SR NO | Chainage | HDD work Required for | Chainage |  | HDD Work with 100 mm HDPE Pipe in Mtr | Remark
|  |  | From | To
1 | Faridpur | For weigh bridge | 266.580 LHS | 266.580 RHS | 40 | With BHS electrical Chamber | 268.13
2 |  | For Highmast & Weigh | 266.580 LHS | 266.790 LHS | 240 | without Chamber
3 |  | Highmast Supply | 266.760 LHS | 266.760 RHS | 100 | For damaged Cable replacement
4 |  | Toll building & Tunel Supply | Electrical Building | admin building near Tunel | 320 | The laying is to be carried out from chamber to chamber at intervals of 30–35 meters. With 2 set Pipe
5 |  | For RHS TMS equipment | 266.920 LHS | 266.920 RHS | 220 | For Spare supply cable laying for RHS with both side chamber in Set | Resuced in PR
6 |  | Highmast Supply | 267.020 LHS | 267.020 LHS | 80 | With BHS electrical Chamber
7 | Maigalganj | For weigh bridge | 371.740 LHS | 371.740 RHS | 40 | With BHS electrical Chamber
8 |  | For Highmast & Weigh | 371.740 LHS | 371.960 LHS | 240 | without Chamber
9 |  | Highmast Supply | 371.935 LHS | 371.935 RHS | 100 | For damaged Cable replacement
10 |  | Toll building & Tunel Supply | Electrical Building | admin building near Tunel | 320 | The laying is to be carried out from chamber to chamber at intervals of 30–35 meters. With 2 set Pipe
11 |  | For RHS TMS equipment | 372.120 LHS | 372.120 RHS | 220 | For Spare supply cable laying for RHS with both side chamber in Set | Resuced in PR
12 |  | Highmast Supply | 372.360 LHS | 372.360 RHS | 80 | With BHS electrical Chamber
Total SUM |  |  |  |  | 2000
317.43
330.4
360.41
360.45
370.8
373.95
387.1
412.27

## HDD 100 & 63mm Pipe for site
HDD Work With 100 mm Dia PN6-8 grade HDPE Pipe for ATMs & Electrical Damaged cable replacement at site
SR NO | Chainage | HDD work Required for | Chainage |  | HDPE Pipe Size | HDD Work with 63 mm HDPE Pipe in Mtr | Remark
|  |  | From | To
4 | 334.25 | For street Light Panel | LHS | RHS | 100 mm | 250
5 | 348.6 | For LED street Light | 348.45 | 348.7 | 63mm | 150
11 | 377.4 | For Highmast Supply | Median | RHS | 63mm | 40
| 392.7 | For Highmast Supply | RHS | LHS | 100mm | 100
12 | 407+650 | For street Light | LHS | Median | 63mm | 40
13 | 407+650 | For Highmast Supply | LHS | RHS | 63mm | 90
Spare | [5 empty] | 330
Total SUM | [5 empty] | 1000 | 500 Mtr reduced from Pr of ATMS

## Electrical Chamber
Construction of Electrical Chamber for Both Toll Plaza from Electrical Building to near Tunel of Admin Building
SR NO | Chainage | Toll Plaza name | Location | Chainage |  | Qty in No's | Remark
|  |  |  | From | To
1 | 266.62 | Faridpur | For Highmast & Weigh Bridge | LHS ROW | RHS ROW | 2 | The chamber will be constructed after the HDD work is completed.
2 | 266.98 |  | Toll Spare Supply | LHS ROW | RHS ROW | 2 | The chamber will be constructed after the HDD work is completed.
| 266.98 |  | for 11 KVA supllly | VCB/HT Meter room | electrical building | 2 | The chamber will be constructed during the laying of HDPE pipe.
3 | 266.98 |  | Faridpur Toll Plaza building & Tunnel Supply | Electrical Building | Near Tunel | 8 | The chamber will be constructed during the laying of HDPE pipe.
4 | 267.2 |  | For Highmast | LHS ROW | RHS ROW | 2 | The chamber will be constructed after the HDD work is completed.
5 | 372.1 | Maigalganj | For Highmast & Weigh Bridge | LHS ROW | RHS ROW | 2 | The chamber will be constructed after the HDD work is completed.
6 | 372.1 |  | Toll Spare Supply | LHS ROW | RHS ROW | 2 | The chamber will be constructed after the HDD work is completed.
|  |  | for 11 KVA supllly | VCB/HT Meter room | electrical building | 2 | The chamber will be constructed during the laying of HDPE pipe.
7 | 372.1 |  | Maigalganj Toll Plaza building & Tunnel Supply | Electrical Building | Near Tunel | 8 | The chamber will be constructed during the laying of HDPE pipe.
8 | 372.35 |  | For Highmast | LHS ROW | RHS ROW | 2 | The chamber will be constructed after the HDD work is completed.
Total SUM | [5 empty] | 32
317.43
330.4
360.41
360.45
370.8
373.95
387.1
412.27

## Earthing for Street Light Pole
Details of Earthing for Street Light Pole, Highmast Pole, Fedder pillar, & Highmast Panel
SR NO | Equipment Name | Chainage | Village Name | Description | Chainage |  |  | Total No of Pole | Total no of Highmast | Earthing Qty. for street Light | Earthing Qty. Street Light feeder & Panel Panel | Earthing Qty. for Highmast Pole | Earthing Qty. for Highmast Panel | 8 Swg GI Wire Pole to Pole Length in Mtr | 8 Swg GI Wire from Feeder Pillar to First Pole Length in Mtr |  | Remark
[5 empty] | From | To | Length in Mtr
1 | LED STREET LIGHT | 262.9 | Kesharpur Truck Lay By | Truck Lay by | 262.9 | 263.15 | 250 | 8 | 0 | 0.88889 | 1 | 0 | 0 |  |  |  |  | Avg considered
2 | Highmast | 266.62 | Faridpur Toll Highmast A1 Side | Toll Plaza Permises | 266.62 | 266.82 | 200 | 0 | 4 | 0 | 1 | 4 | 1
3 | Toll Plaza | 266.98 | Toll Plaza | Faridpur Toll Plaza | 266.82 | 266.98 | 160 | 0 | 4 | 0 | 1 | 4 | 1
4 | Highmast | 267.16 | Faridpur Toll Toll Highmast A2 Side | Toll Plaza Permises | 267.1 | 267.29 | 190 | 0 | 4 | 0 | 1 | 4 | 1
5 | Highmast | 268.15 | Gausganj Sarai near Khandelwal Oils | Junction RHS | 268.15 | 268.15 | 0 | 0 | 1 | 0 | 1 | 1 | 1
6 | HPSV STREET LIGHT | 270 | Faridpur Bypass Bareilly | Flyover/VUP | 269.7 | 270.35 | 650 | 26 | 2 | 2.8889 | 2 | 2 | 2 | 675 | 40
7 | Highmast | 272.5 | Kshatripati Shiva Ji inter collage | Junction RHS | 272.52 | 272.52 | 0 | 0 | 1 | 0 | 1 | 1 | 1
8 | HPSV STREET LIGHT | 274.17 | NEAR GURUDWARA FARIDPUR | Flyover/VUP | 273.7 | 274.45 | 750 | 28 | 1 | 3.1111 | 2 | 1 | 1 | 725 | 50
9 | HPSV STREET LIGHT | 277.66 | Faridpur Bareilly | Flyover/VUP | 277.3 | 278.1 | 800 | 28 | 2 | 3.1111 | 2 | 2 | 2 | 725 | 40
10 | HPSV STREET LIGHT | 282.38 | NEELAM VENEER, Stiswa | Flyover/VUP | 282 | 282.8 | 800 | 29 | 2 | 3.2222 | 2 | 2 | 2 | 750 | 50
11 | HPSV STREET LIGHT | 288.2 | Uchesiya Mod Fatehganj Purbi Near Gupta Restourent | Flyover/VUP | 287.85 | 288.65 | 800 | 29 | 2 | 3.2222 | 2 | 2 | 2 | 750 | 40
12 | HPSV STREET LIGHT | 289.12 | Fatehganj Purbi | Flyover/VUP | 288.9 | 289.5 | 600 | 22 | 0 | 2.4444 | 2 | 0 | 0 | 575 | 50
13 | LED STREET LIGHT | 290.6 | Shalpur Navdia ROB | Flyover/ROB | 290.05 | 291.35 | 1300 | 166 | 0 | 11.0667 | 1 | 0 | 0
14 | HPSV STREET LIGHT | 295.37 | Katara | Flyover/VUP | 295 | 295.73 | 730 | 60 | 2 | 5.4545 | 2 | 2 | 2 | 1525 | 50
15 | HPSV STREET LIGHT | 303.65 | Mansoorpur Tilhar Cut | Flyover/VUP | 303.25 | 303.95 | 700 | 26 | 1 | 2.8889 | 2 | 1 | 1 | 675 | 50
16 | HPSV STREET LIGHT | 305.41 | Tilahar BHS | Flyover/VUP | 305.05 | 305.9 | 850 | 74 | 2 | 6.7273 | 2 | 2 | 2 | 1875 | 50
17 | LED STREET LIGHT | 306.1 | Tilhar City Rd Truck Lay By | Truck Lay by | 306.15 | 306.3 | 150 | 8 | 0 | 0.88889 | 1 | 0 | 0
18 | Highmast | 307 |  | Junction RHS | 307 | 307 | 0 | 0 | 1 | 0 | 1 | 1 | 1
19 | LED STREET LIGHT | 314.64 | Street Light | Flyover/VUP | 314.3 | 314.9 | 600 | 36 | 0 | 4 | 1 | 0 | 0
20 | HPSV STREET LIGHT | 315.75 | Banthara | Flyover/VUP | 315.35 | 316 | 650 | 58 | 2 | 6.4444 | 2 | 2 | 2 | 1475 | 50
21 | Highmast | 317.42 | HIGHMAST LHS | Junction LHS | 317.42 | 317.42 | 0 | 0 | 1 | 0 | 1 | 1 | 1
22 | HPSV STREET LIGHT | 325.58 | Bareilly Mod BHS | Flyover/VUP | 325.1 | 326 | 900 | 62 | 2 | 5.6364 | 2 | 2 | 2 | 1575 | 50
23 | HPSV STREET LIGHT | 329.56 | Near BHARAT DHABA BRIDGE BHS | Flyover/VUP | 329.1 | 330 | 900 | 69 | 2 | 6.2727 | 2 | 2 | 2 | 1750 | 40
24 | Highmast | 331.7 | ATSALIYA LHS | Junction RHS | 334.9 | 334.9 | 0 | 0 | 1 | 0 | 1 | 1 | 1
25 | HPSV STREET LIGHT | 331.95 | NEAR DOON SCHOOL BHS, Ahmadpur Niwazpur | Flyover/VUP | 331.6 | 332.5 | 900 | 66 | 4 | 6 | 4 | 4 | 4 | 1675 | 50
26 | HPSV STREET LIGHT | 334.25 | ROB RAILWAY CROSSING, LHS | Flyover/ROB | 333.7 | 334.9 | 1200 | 70 | 1 | 6.3636 | 2 | 1 | 1 | 1775 | 50
27 | Highmast | 334.9 |  | Junction LHS | 334.9 | 334.9 |  |  | 1 | 0 | 1 | 1 | 1
28 | HPSV STREET LIGHT | 336.65 | Jamuhi, Shajahanpur Rd | Flyover/VUP | 336.3 | 337.1 | 800 | 66 | 1 | 6 | 1 | 1 | 1 | 1675 | 25
29 | LED STREET LIGHT | 348.6 | Uncholia,, Gurudwara | Truck Lay by | 348.45 | 348.7 | 250 | 16 | 0 | 1.7778 | 1 | 0 | 0
30 | Highmast | 356.35 | PANAI CHAURAHA | Junction RHS | 356.35 | 356.35 | 0 | 0 | 1 | 0 | 1 | 1 | 1
31 | HPSV STREET LIGHT | 358.05 | Barkheriya Jat | Flyover/VUP | 357.6 | 358.45 | 850 | 33 | 2 | 3.6667 | 2 | 2 | 2 | 850 | 50
32 | Highmast | 360.57 | Udaypur, JB Ganj Khad Godam | Junction RHS | 360.57 | 360.57 | 0 | 0 | 1 | 0 | 1 | 1 | 1
33 | Highmast | 361.6 | Highmast BHS | Flyover/VUP | 361.6 | 361.6 | 0 | 0 | 2 | 0 | 1 | 2 | 2
34 | HPSV STREET LIGHT | 363.65 | Hariyali mod | Flyover/VUP | 363.4 | 363.95 | 550 | 21 | 2 | 2.3333 | 2 | 2 | 1 | 550 | 50
35 | Highmast | 365.45 | Pihani Mod | Flyover/VUP | 365.45 | 365.45 | 0 | 0 | 2 | 0 | 1 | 2 | 1
36 | HPSV STREET LIGHT | 370.1 | Chapartala, Near Toll | Flyover/VUP | 369.65 | 370.7 | 1050 | 43 | 2 | 4.7778 | 2 | 2 | 1 | 1100 | 40
37 | LED STREET LIGHT | 370.7 | Chapartala, Near Toll | Truck Lay by | 370.7 | 371.7 | 1000 | 8 | 0 | 0.88889 | 1 | 0 | 0
38 | Highmast | 372.1 | Aurangabad Khiri | Toll Plaza Permises | 371.75 | 371.92 | 170 | 0 | 4 | 0 | 1 | 4 | 1
39 | Toll Plaza | 372.1 | Toll Plaza Maigalganj | Maigalganj Toll Plaza | 372.02 | 372.18 | 160 | 0 | 4 | 0 | 1 | 4 | 1
40 | Highmast | 372.35 | Maigalganj Toll, Highmast Sitapur Side | Toll Plaza Permises | 372.26 | 372.48 | 220 | 0 | 4 | 0 | 1 | 4 | 1
41 | Highmast | 374.08 | Rahjaniya, Maigalganj | Junction RHS | 374.08 | 374.08 | 0 | 0 | 1 | 0 | 1 | 1 | 1
42 | HPSV STREET LIGHT | 377.35 | Aurangabad / Maigalganj Bypass | Flyover/VUP | 376.8 | 378 | 1200 | 45 | 2 | 5 | 2 | 2 | 1 | 1150 | 40
43 | Highmast | 380.05 | Highmast RHS | Junction RHS | 380.05 | 380.05 | 0 | 0 | 1 | 0 | 1 | 1 | 1
44 | LED STREET LIGHT | 382.75 | Truck Lay By | Truck Lay By | 382.45 | 382.7 | 250 | 8 | 0 | 0.88889 | 1 | 0 | 0
45 | HPSV STREET LIGHT | 383.65 | Neri, Maholi | Flyover/VUP | 383.2 | 384.2 | 1000 | 42 | 2 | 4.6667 | 2 | 2 | 1 | 1075 | 50
46 | HPSV STREET LIGHT | 388.13 | Bhudiya PO Kachuri, Sitapur | Flyover/VUP | 387.8 | 388.6 | 800 | 32 | 2 | 3.5556 | 2 | 2 | 1 | 825 | 40
47 | HPSV STREET LIGHT | 392.47 | Badagaon Maholi | Flyover/VUP | 391.9 | 393 | 1100 | 41 | 2 | 4.5556 | 2 | 2 | 1 | 1050 | 50
48 | Highmast | 395.55 | Maholi, Sitapur | Junction RHS | 395.55 | 395.55 | 0 | 0 | 1 | 0 | 1 | 1 | 1
49 | HPSV STREET LIGHT | 396.2 | Maholi BHS | Flyover/VUP | 395.75 | 396.6 | 850 | 64 | 1 | 5.8182 | 2 | 1 | 1 | 1625 | 40
50 | HPSV STREET LIGHT | 401.45 | Street Light MEDIAN | Flyover/VUP | 401.1 | 402 | 900 | 35 | 2 | 3.8889 | 2 | 2 | 1 | 900 | 50
51 | LED STREET LIGHT | 403.4 | Hempur ROB RHS | ROB | 402.6 | 404 | 1400 | 118 |  | 7.8667 | 1 | 0 | 0
52 | Highmast | 403.57 | Hempur Highmast | Junction RHS | 403.57 | 403.57 | 0 | 0 | 1 | 0 | 1 | 1 | 1
53 | HPSV STREET LIGHT | 407.6 | Katili Bridge BHS | Flyover/VUP | 407.29 | 408 | 710 | 55 | 2 | 6.1111 | 2 | 2 | 1 | 1400 | 40
54 | Highmast | 412.45 | Kashiram Colony, Sitapur | Junction LHS | 412.45 | 412.45 | 0 | 0 | 1 | 0 | 1 | 1 | 1
55 | LED STREET LIGHT | 413.83 | Naveen Chowk, VUP | VOP | 413.83 | 413.83 | 0 | 30 |  | 3.3333 | 1 | 0 | 0
56 | Highmast | 413.9 | Naveen Chowk Highmast | Junction LHS | 413.83 | 413.83 | 0 | 0 | 1 | 0 | 1 | 1 | 1
57 | LED STREET LIGHT | 416.65 | Bahuguda Chauraha Bridge | Flyover/VUP | 416.34 | 417.06 | 720 | 58 | 0 | 6.4444 | 1 | 0 | 0
58 | HPSV STREET LIGHT | 417.8 | kamta sariya-1 | Flyover/VUP | 417.35 | 418.35 | 1000 | 40 | 2 | 4.4444 | 2 | 2 | 1 | 1025 | 50
59 | HPSV STREET LIGHT | 418.75 | kamta sariya-2 | Flyover/VUP | 418.35 | 419.35 | 1000 | 40 | 1 | 4.4444 | 2 | 1 | 1 | 1025 | 40
Total Sum | [7 empty] | 1660 | 90 | 161.0949 | 87 | 90 | 62 | 30775 | 1225 | 0
Total no of Earthing for Street Light Pole, Highmast Pole, Fedder pillar, & Highmast Panel | [9 empty] | 400 |  |  |  | 32000

## Earthing at Toll Plaza & GI wi
Earthing Work at Both Toll Plaza
SR NO | Location | Earthing Eaquipment Name | Type of earthing | Qty of GI Earthing in No's | Qty of Cu Earthing in No's | Qty of GI Strip in Mtr | Qty of Cu Strip in Mtr | Qty of Cu insulated Cable 70 Sq mm in Mtr | Qty of Cu insulated Wire 4 Sq mm in Mtr | GI wire | Remark
1 | Faridpur Toll Plaza | Transformer Neautral earthing Earthing | Copper Chemical Electrode |  | 1 |  | 15
2 | Faridpur Toll Plaza | Transformer Body earthing Earthing | GI Chemical Electrode | 2 |  | 30
3 | Faridpur Toll Plaza | Cubical Energy Meter Body Earthing | GI Chemical Electrode | 2 |  | 30
4 | Faridpur Toll Plaza | 11 KVA VCB Panel Panel Body Earthing | GI Chemical Electrode | 2 |  | 30
5 | Faridpur Toll Plaza | 250 KVA Stabilizer Body Earthing | GI Chemical Electrode | 1 |  | 15
6 | Faridpur Toll Plaza | AMF/LTDB/APFC Panel Body Earthing | GI Chemical Electrode | 1 |  | 15
7 | Faridpur Toll Plaza | DG-1 Neutral Earthing | Copper Chemical Electrode |  | 1 |  | 15
8 | Faridpur Toll Plaza | DG-2 Neutral Earthing | Copper Chemical Electrode |  | 1 |  | 15
9 | Faridpur Toll Plaza | DG-1 Body Earthing | GI Chemical Electrode | 2 |  | 30
10 | Faridpur Toll Plaza | DG-2 Body Earthing | GI Chemical Electrode | 2 |  | 30
11 | Faridpur Toll Plaza | Admin Buiding earthing | Copper Chemical Electrode |  | 2 |  | 15 |  | 20
12 | Faridpur Toll Plaza | LA Earthing of Electrical Building | Copper Chemical Electrode |  | 3 |  | 15 | 50
13 | Faridpur Toll Plaza | Highmast Pole & Panel Body Earthing | GI Chemical Electrode | 12 |  | 48
14 | Faridpur Toll Plaza | Weight Bridge building & SPD LHS | GI Chemical Electrode | 2 |  | 10 |  |  | 20
15 | Faridpur Toll Plaza | Weight Bridge building & SPD RHS | GI Chemical Electrode | 2 |  | 10 |  |  | 20
16 | Maigalganj Toll Plaza | Transformer Neautral earthing Earthing | Copper Chemical Electrode |  | 1 |  | 15
17 | Maigalganj Toll Plaza | Transformer Body earthing Earthing | GI Chemical Electrode | 2 |  | 30
18 | Maigalganj Toll Plaza | Cubical Energy Meter Body Earthing | GI Chemical Electrode | 2 |  | 30
19 | Maigalganj Toll Plaza | 11 KVA VCB Panel Panel Body Earthing | GI Chemical Electrode | 2 |  | 30
20 | Maigalganj Toll Plaza | 250 KVA Stabilizer Body Earthing | GI Chemical Electrode | 1 |  | 15
21 | Maigalganj Toll Plaza | AMF/LTDB/APFC Panel Body Earthing | GI Chemical Electrode | 1 |  | 15
22 | Maigalganj Toll Plaza | DG-1 Neutral Earthing | Copper Chemical Electrode |  | 1 |  | 15
23 | Maigalganj Toll Plaza | DG-2 Neutral Earthing | Copper Chemical Electrode |  | 1 |  | 15
24 | Maigalganj Toll Plaza | DG-1 Body Earthing | GI Chemical Electrode | 2 |  | 30
25 | Maigalganj Toll Plaza | DG-2 Body Earthing | GI Chemical Electrode | 2 |  | 30
26 | Maigalganj Toll Plaza | Admin Buiding earthing | Copper Chemical Electrode |  | 2 |  | 15 |  | 20
27 | Maigalganj Toll Plaza | LA Earthing of Electrical Building | Copper Chemical Electrode |  | 3 |  | 15 | 50
28 | Maigalganj Toll Plaza | Highmast Pole & Panel Body Earthing | GI Chemical Electrode | 12 |  | 48
29 | Maigalganj Toll Plaza | Weight Bridge building & SPD LHS | GI Chemical Electrode | 2 |  | 10 |  |  | 20
30 | Maigalganj Toll Plaza | Weight Bridge building & SPD RHS | GI Chemical Electrode | 2 |  | 10 |  |  | 20
Spare | [5 empty] | 1304 |  | 50 |  | 5200 | For site panel & highmast Pole
TOTAL |  |  |  | 56 | 16 | 1800 | 150 | 150 | 120 | 5200

## Damage Pole
Location of Damaged Pole
Sr. No. | Chainage | Side | Arm Type | Foundation/ Bracket | QTY of Damaged Pole | Damaged Pole Availavle at Site | Photo | Location | Remark
1 | 273+850 | Median | Double Arm | Foundation | 1 | 1 |  | 005 Reshambaag Near Katra Raod, Bareilly Reshambaag, near Katra Raod, Bakainiya, Uttar Pradesh 243503 | Pole & Foundation Damaged
2 | 273+880 | Median | Double Arm | Foundation | 1 | 1 |  | 005 Reshambaag Near Katra Raod, Bareilly Reshambaag, near Katra Raod, Bakainiya, Uttar Pradesh 243503 | Pole & Foundation Damaged
3 | 274+000 | Median | Double Arm | Foundation | 1 | 1
4 | 274+220 | Median | Double Arm | Foundation | 1 | 1 |  | NH 30, Bakainiya, Uttar Pradesh 243503 | Pole & Foundation Damaged
5 | 277+600 | Median | Double Arm | Foundation | 1 | 1 |  | NH 730C, Bhagwanpur Phulwa, Uttar Pradesh 243503 | Pole & Foundation Damaged
6 | 278+120 | Median | Double Arm | Foundation | 1 | 1 |  | Bhagwanpur Phulwa, Uttar Pradesh 243503 | Pole & Foundation Damaged
7 | 282+100 | Median | Double Arm | Foundation | 1 | 1
8 | 288+150 | Median | Double Arm | Foundation | 1 | 1 |  | Fatehganj Purvi, Uttar Pradesh 243506 | Pole Damaged
9 | 288+125 | Median | Double Arm | Foundation | 1 |  |  | Fatehganj Purvi, Uttar Pradesh 243506 | Pole Damaged
10 | 288+100 | Median | Double Arm | Foundation | 1 | 1 |  | Fatehganj Purvi, Uttar Pradesh 243506 | Pole & Foundation Damaged
11 | 288+075 | Median | Double Arm | Foundation | 1 | 1 |  | Fatehganj Purvi, Uttar Pradesh 243506 | Pole & Foundation Damaged
12 | 290+660 | RHS | Single Arm | Bracket | 1 | 1 |  | NH 730C, Heerpur, Uttar Pradesh 242301 | Pole Lay down due to bracket damaged
13 | 290+000 | LHS | Single Arm | Foundation | 1 | 1 |  | 01, Main Market Fatehganj Eest 01, Main Market, Eest, Fatehganj, Heerpur, Uttar Pradesh 242301 | Pole & Foundation Damaged
14 | 290+100 | LHS | Single Arm | Foundation | 1 | 1
15 | 290+100 | RHS | Single Arm | Foundation | 1 | 1 |  | 01, Main Market Fatehganj Eest 01, Main Market, Eest, Fatehganj, Heerpur, Uttar Pradesh 242301 | Pole & Foundation Damaged
16 | 290+100 | RHS | Single Arm | Foundation | 1 | 1 |  | 01, Main Market Fatehganj Eest 01, Main Market, Eest, Fatehganj, Heerpur, Uttar Pradesh 242301 | Pole & Foundation Damaged
17 | 290+440 | LHS | Single Arm | Bracket | 1 | 1 |  |  | Pole & Foundation Damaged
18 | 290+600 | LHS | Single Arm | Bracket | 1 | 1 |  |  | Pole collaps due to storm
19 | 290+800 | RHS | Single Arm | Bracket | 1 | 1
20 | 303+370 | Median | Double Arm | Foundation | 1 | 1 |  | G T Road, Tilhar 242301 | Pole Collaps
21 | 303+395 | Median | Double Arm | Foundation | 1 | 1 |  | G T Road, Tilhar 242301 | Pole & Foundation Damaged
22 | 303+540 | Median | Double Arm | Foundation | 1 | 1 |  | Mustafabad Urf Bhureli, Uttar Pradesh 242307 | Pole Collaps
23 | 303+565 | Median | Double Arm | Foundation | 1 | 1 |  | Mustafabad Urf Bhureli, Uttar Pradesh 242307 | Pole Collaps
24 | 303+640 | Median | Double Arm | Foundation | 1 |  |  | Tilhar City Rd, Mansoorpur, Tilhar, Uttar Pradesh 242307 | Pole & Foundation Damaged
25 | 303+640 | Median | Double Arm | Foundation | 1 | 1 |  | Tilhar City Rd, Mansoorpur, Tilhar, Uttar Pradesh 242307 | Pole Collaps
26 | 303+320 | Median | Double Arm | Foundation | 1 | 1 |  | G T Road, Tilhar 242301 | Pole Collaps
27 | 303+350 | Median | Double Arm | Foundation | 1 | 1 |  | G T Road, Tilhar 242301 | Pole Collaps
28 | 303+350 | Median | Double Arm | Foundation | 1 | 1 |  | G T Road, Tilhar 242301 | Pole Collaps
29 | 303+370 | Median | Double Arm | Foundation | 1 | 1 |  | G T Road, Tilhar 242301 | Pole & Foundation Damaged
30 | 305+850 | LHS | Double Arm | Foundation | 1 | 1 |  | NH30 bypass chauraha, Tilhar, Uttar Pradesh 242307 | Pole Damaged
31 | 314+600 | RHS | Single Arm | Bracket | 1 |  |  | WRF8+65 Railway Crossing Flyover, Banthara, Uttar Pradesh 242307 | Bracket Pole Damaged
32 | 337+020 | RHS | Double Arm | Foundation | 1 |  |  | NH24, Doraha, Jamuka, Uttar Pradesh 242306 | Pole Damaged
33 | 348+600 | LHS | Single Arm | Foundation | 3
34 | 357+900 | Median | Double Arm | Foundation | 1 |  |  | Barkheriya Jat
35 | 358+100 | Median | Double Arm | Foundation | 1 | 1
36 | 358+420 | Median | Double Arm | Foundation | 2 |  |  | Barkheriya Jat
37 | 363+400 | Median | Double Arm | Foundation | 2 |  |  | Mahmoodpur Saraiyan
38 | 369+820 | Median | Double Arm | Foundation | 1 | 1 |  | Chhapartala, Maigalganj
39 | 370+200 | Median | Double Arm | Foundation | 1 |  |  | Chhapartala, Maigalganj
40 | 370+700 | Median | Double Arm | Foundation | 1 |  |  | Chhapartala, Maigalganj
41 | 376+800 | Median | Double Arm | Foundation | 1 |  |  | Maigalganj -Aurangabaad Bypass
42 | 377+000 | Median | Double Arm | Foundation | 1 | 1 |  | Maigalganj -Aurangabaad Bypass
43 | 377+350 | Median | Double Arm | Foundation | 1 | 1 |  | Maigalganj -Aurangabaad Bypass
44 | 382.75 | Median | Double Arm | Foundation | 2 | 2 |  | Neri
45 | 383.65 | Median | Double Arm | Foundation | 1 |  |  | Neri
46 | 387+800 | Median | Double Arm | Foundation | 1 |  |  | Bhudiya PO Kachuri,
47 | 387+800 | Median | Double Arm | Foundation | 1 | 1 |  | Bhudiya PO Kachuri,
48 | 387+800 | Median | Double Arm | Foundation | 1 | 1 |  | Bhudiya PO Kachuri,
49 | 388.13 | Median | Double Arm | Foundation | 1 |  |  | Bhudiya PO Kachuri,
50 | 392+380 | Median | Double Arm | Foundation | 1 |  |  | Maholi Bridge
51 | 392+400 | Median | Double Arm | Foundation | 1 | 1 |  | Maholi Bridge
52 | 392+470 | Median | Double Arm | Foundation | 1 | 1 |  | Maholi Bridge
53 | 392+600 | Median | Double Arm | Foundation | 1 | 1 |  | Maholi Bridge
54 | 401+600 | Median | Double Arm | Foundation | 1 | 1 |  | Bagaha
55 | 403+100 | RHS | Differencial | Bracket | 2 | 2
56 | 403+125 | RHS | Differencial | Bracket | 1 | 1
57 | 403+200 - 403+600 | RHS | Differencial | Bracket | 2 | 2
58 | 402+95 | RHS | Single Arm | Foundation | 3 | 3
59 | 417+400 | Median | Double Arm | Foundation | 1 | 1 |  | kamta sariya-1
60 | 418+650 | Median | Double Arm | Foundation | 1 | 1 |  | kamta sariya-2
| Spare |  | Double Arm | Foundation | 31 | 10
Total |  |  |  |  | 100 | 60

## Copper Flexi cable
Copper Flexi Cable 3X1.5 Sq. mm Supply & Installation of 3Cx1.5 sq. Cu Flexible FRLS Wire for connection of light fitting. ( From Pole Junction Box to light fixtures)
SR NO | Equipment Name | Chainage | Village Name | Description | Chainage |  |  | Total No of Pole | Total No of Light Fixture | Copper Flexi Cable 3X1.5 Sq. mm | Remark
[5 empty] | From | To | Length in Mtr
1 | LED STREET LIGHT | 262.9 | Kesharpur Truck Lay By | Truck Lay by | 262.9 | 263.15 | 250 | 8 | 8 | 104 | Pole height 10 m & arm height 2-.2.5 m
13 | LED STREET LIGHT | 290.6 | Shalpur Navdia ROB | Flyover/ROB | 290.05 | 291.35 | 1300 | 166 | 166 | 2158
17 | LED STREET LIGHT | 306.1 | Tilhar City Rd Truck Lay By | Truck Lay by | 306.15 | 306.3 | 150 | 8 | 8 | 104
19 | LED STREET LIGHT | 314.64 | Street Light | Flyover/VUP | 314.3 | 314.9 | 600 | 36 | 72 | 936
29 | LED STREET LIGHT | 348.6 | Uncholia,, Gurudwara | Truck Lay by | 348.45 | 348.7 | 250 | 16 | 16 | 208
37 | LED STREET LIGHT | 370.7 | Chapartala, Near Toll | Truck Lay by | 370.7 | 371.7 | 1000 | 8 | 8 | 104
44 | LED STREET LIGHT | 382.75 | Truck Lay By | Truck Lay By | 382.45 | 382.7 | 250 | 8 | 8 | 104
51 | LED STREET LIGHT | 403.4 | Hempur ROB RHS | ROB | 402.6 | 404 | 1400 | 118 | 236 | 3068
55 | LED STREET LIGHT | 413.83 | Naveen Chowk, VUP | VOP | 413.83 | 413.83 | 0 | 30 | 75 | 975
57 | LED STREET LIGHT | 416.65 | Bahuguda Chauraha Bridge | Flyover/VUP | 416.34 | 417.06 | 720 | 58 | 116 | 1508
Spare for toll & Site For installation | [9 empty] | 2731
Total | [9 empty] | 12000

## Damaged Arm
Damaged Arm & Missing Light Details
Sr.No | Chainage | Side | Arm Type | Damaged Arm | Missing Light | Photo | Location | Remark
1 | 274+280 | Median | Double Arm | 1 | 2 |  | NH 30, Bakainiya, Uttar Pradesh 243503 | Pole arm damage
2 | 303+580 | Median | Double Arm | 1 | 1 |  | 0, Tilhar, Uttar Pradesh 242307 | Pole arm damage
3 | 329+660 to 330 +00 | RHS | Flexi Arm | 1 | 3 |  | Hardoi Bypass, Saraikaiyan, Shahjahanpur, Uttar Pradesh 242406 | 1 Arm missing 3 light missing R H S
4 | 329+840 | RHS | Flexi Arm | 2 | 2 |  | Bypass churaha hardoi, Shahjahanpur Bypass Rd, Shahjahanpur, Uttar Pradesh 242406 | 2 Arm missing
5 | 331+900 | RHS | Differencial Arm | 1 | 1 |  | 05, Roza, Ahmadpur Niwazpur, Shahjahanpur, Uttar Pradesh 242406 | 1 light missing
6 | 383+350 | Median | Double Arm | 8 | 16 |  | Neri
7 | Spare |  |  | 10 | 20
Total |  |  |  | 24 | 45

## 200W LED Installation
Required Total installation of 200 W LED Light fixture in place of 400W HPSV
SR NO | Equipment Name | Chainage | Village Name | Division | Connection No. | Meter Sr No | Sanction Load | Chainage |  |  | No Of Existiong Pole |  |  |  |  | Light Fixture Watt | Total no of Pole | Total No Required 200 W LED Light Fixture | Remark
[11 empty] | Single Arm |  | Double/Differential Arm
[8 empty] | From | To | Length in Mtr | LHS | RHS | LHS | Median | RHS
1 | HPSV STREET LIGHT | 270.1 | Faridpur Bypass Bareilly | EDD-BAREILLY-II | 4955777655 | 8572984 | 20 KW | 269.7 | 270.35 | 650 |  |  |  | 26 |  | 400 | 26 | 52
2 | HPSV STREET LIGHT | 274.17 | NEAR GURUDWARA FARIDPUR | EDD-BAREILLY-II | 1571806643 | 1250104 | 23 KW | 273.7 | 274.45 | 750 |  |  |  | 28 |  | 400 | 28 | 56
3 | HPSV STREET LIGHT | 277.75 | Faridpur Bareilly | EDD-BAREILLY-II | 0225766798 | 1251414 | 10 KW | 277.3 | 278.1 | 800 |  |  |  | 28 |  | 400 | 28 | 56
4 | HPSV STREET LIGHT | 282.38 | NEELAM VENEER, Tisuwa | EDD-BAREILLY-II | 3163720980 | 1250177 | 28 KW | 282 | 282.8 | 800 |  |  |  | 29 |  | 400 | 29 | 58
5 | HPSV STREET LIGHT | 288.2 | Uchesiya Mod Fatehganj Purbi Near Gupta Restourent | EDD-BAREILLY-II | Connection ID NA | SS21684963 |  | 287.85 | 288.65 | 800 |  |  |  | 29 |  | 400 | 29 | 58
6 | HPSV STREET LIGHT | 289.12 | Fatehganj Purbi | EDD-BAREILLY-II | 6208633634 | 8574560 | 15 KW | 288.9 | 289.5 | 600 |  |  |  | 22 |  | 400 | 22 | 44
7 | HPSV STREET LIGHT | 295.37 | Katara Chauraha LHS | TILHAR | 5372229478 | 2333972 AL2716531 | 30 KW | 295 | 295.73 | 730 |  |  | 30 |  |  | 400 | 30 | 60
8 | HPSV STREET LIGHT | 295.37 | Katara Chauraha RHS | TILHAR | 1459923079 | 9305779 | 30 KW | 295 | 295.73 | 730 |  |  |  |  | 30 | 400 | 30 | 60
9 | HPSV STREET LIGHT | 303.65 | Mansoorpur Tilhar Cut | TILHAR | Connection ID NA | 01504441 '01504442 | 35 KW | 303.25 | 303.95 | 700 |  |  |  | 26 |  | 400 | 26 | 52
10 | HPSV STREET LIGHT | 305.44 | Tilahar LHS | TILHAR | Connection ID NA | 9084719 9084801 | 30 KW | 305.05 | 305.9 | 850 |  |  | 37 |  |  | 400 | 37 | 74
11 | HPSV STREET LIGHT | 305.41 | Tilahar RHS | TILHAR | 2419462491 | 01504290 | 30 KW | [7 empty] | 37 | 400 | 37 | 74
12 | LED STREET LIGHT | 314.64 | Street Light | EDD I SHAHJAHANPUR | Connection ID NA | 21012086 21012085 |  | 314.3 | 314.9 | 600 |  |  | 19 |  | 17 | 250 | 36 | 72
13 | HPSV STREET LIGHT | 315.75 | Banthara | EDD I SHAHJAHANPUR | 9469457893 | 3612728 |  | 315.35 | 316 | 650 |  |  | 29 |  | 29 | 400 | 58 | 116
14 | HPSV STREET LIGHT | 325.58 | Bareilly Mod LHS | EDD I SHAHJAHANPUR | 5009545020 | 3612730 | 20 kW | 325.1 | 326 | 900 |  |  | 32 |  |  | 400 | 32 | 64
15 | HPSV STREET LIGHT | 325.63 | Bareilly Mod RHS | EDD I SHAHJAHANPUR | 5391347848 | 3612731 | 20 kW | [7 empty] | 30 | 400 | 30 | 60
16 | HPSV STREET LIGHT | 329.56 | Near BHARAT DHABA BRIDGE LHS | EDD-II, Bahadurganj, Shajhanpur | 1258496779 | X2333856 | 30 kW | 329.1 | 330 | 900 |  |  | 34 |  |  | 400 | 34 | 68
17 | HPSV STREET LIGHT | 329.56 | Roza Bypass RHS | EDD-II, Bahadurganj, Shajhanpur | 9848036325 | X2333991 | 30 kW | 329.1 | 330 | 900 |  |  |  |  | 35 | 400 | 35 | 70
18 | HPSV STREET LIGHT | 331.95 | NEAR DOON SCHOOL LHS, Ahmadpur Niwazpur | EDD-II, Bahadurganj, Shajhanpur | 4548561751 | X2333951 | 30 kW | 331.6 | 332.05 | 450 |  |  | 17 |  |  | 400 | 17 | 34
19 | HPSV STREET LIGHT | 331.95 | NEAR DOON SCHOOL RHS Ahmadpur Niwazpur | EDD-II, Bahadurganj, Shajhanpur | 3254860895 | bill X2333925/ in meter X2333825 | 30 kW | 331.6 | 332.05 | 450 |  |  |  |  | 16 | 400 | 16 | 32
20 | HPSV STREET LIGHT | 332.25 | Honda Colony, Roza - 2 LHS Mandi Marg | EDD-II, Bahadurganj, Shajhanpur | 9945292476 | X2734098 | 30 kW | 332.05 | 332.5 | 450 |  |  | 16 |  |  | 400 | 16 | 32
21 | HPSV STREET LIGHT | 332.25 | Kuda Plant, Roza -1 RHS Mandi Marg | EDD-II, Bahadurganj, Shajhanpur | 0539919387 | X2333876 | 30 kW | 332.05 | 332.5 | 450 |  |  |  |  | 17 | 400 | 17 | 34
22 | HPSV STREET LIGHT | 334.25 | ROB RAILWAY CROSSING, LHS | EDD-II, Bahadurganj, Shajhanpur | 0851833728 | X2333752 | 30 kW | 333.7 | 334.9 | 1200 |  |  | 36 |  | 34 | 400 | 70 | 140
23 | HPSV STREET LIGHT | 336.65 | Jamuhi, Shajahanpur Rd | EDD-II, Bahadurganj, Shajhanpur | 1159634807 | CA0067214 |  | 336.3 | 337.1 | 800 |  |  | 33 |  | 33 | 400 | 66 | 132
24 | HPSV STREET LIGHT | 358.05 | Barkheriya Jat | EDD-II Mohammadi | 7940728214 | 01498184 | 10 KW | 357.6 | 358.45 | 850 |  |  |  | 33 |  | 400 | 33 | 66
25 | HPSV STREET LIGHT | 363.65 | Highmast RHS | Shahabad, Hardoi | 0277502983 | 8421364 | new found | 363.4 | 363.95 | 550 |  |  |  | 21 |  | 400 | 21 | 42
26 | HPSV STREET LIGHT | 370.1 | Chhapartala | EDD-II Mohammadi | 1496937181 | AL2790038 | new found | 369.65 | 370.7 | 1050 |  |  |  | 43 |  | 400 | 43 | 86
27 | HPSV STREET LIGHT | 377.4 | Aurangabad / Maigalganj Bypass | EDD-II Mohammadi | 6454321656 | 01498208 AL2789021 | 10 KW | 376.8 | 378 | 1200 |  |  |  | 45 |  | 400 | 45 | 90
28 | HPSV STREET LIGHT | 383.65 | Neri, Maholi | EDD-I SITAPUR | 0007078076 | X2332906 | 40 kW | 383.2 | 384.2 | 1000 |  |  |  | 42 |  | 400 | 42 | 84
29 | HPSV STREET LIGHT | 388.13 | Bhudiya PO Kachuri, Sitapur | EDD-I SITAPUR | 3118405607 | X2332904 | 30 kW | 387.8 | 388.6 | 800 |  |  |  | 32 |  | 400 | 32 | 64
30 | HPSV STREET LIGHT | 392.47 | Badagaon Maholi | EDD-I SITAPUR | 4763126954 | X2332611 | 40 kW | 391.9 | 393 | 1100 |  |  |  | 41 |  | 400 | 41 | 82
31 | HPSV STREET LIGHT | 396.2 | Maholi LHS | EDD-I SITAPUR | 0193427051 | X2332573 | 30 kVA | 395.75 | 396.6 | 850 |  |  | 32 |  |  | 400 | 32 | 64
32 | HPSV STREET LIGHT | 396.2 | Maholi RHS | EDD-I SITAPUR | 2930129477 | X2332958 | 30 kW | 395.75 | 396.6 | 850 |  |  |  |  | 32 | 400 | 32 | 64
33 | HPSV STREET LIGHT | 401.45 | RICHHAI CHAURAHA | EDD-I SITAPUR | 6124797709 | X2332947 | 40 kW | 401.1 | 402 | 900 |  |  |  | 35 |  | 400 | 35 | 70
34 | HPSV STREET LIGHT | 407.57 | Katili Bridge LHS | EDD-I SITAPUR | 2538736429 | Bill '01494360 site '01494361 | 20 kW | 407.29 | 408 | 710 |  |  | 27 |  |  | 400 | 27 | 54
35 | HPSV STREET LIGHT | 407 | PAPER MILL BRIDGE II, KATILI RHS | EDD-I SITAPUR | 5883292673 | 01494362 | 20 kW | 407.29 | 408 | 710 |  |  |  |  | 28 | 400 | 28 | 56
36 | HPSV STREET LIGHT | 417.8 | Bahuguda Chauraha Bridge | EDD-I SITAPUR | 9652721835 | SS21686440 | 30 kW | 417.35 | 418.05 | 700 |  |  |  | 26 |  | 400 | 26 | 52
37 | HPSV STREET LIGHT | 418.7 | kamta sariya-1 | EDD-I SITAPUR | 5958274382 | SS21686436 | 30 kW | 418.05 | 418.75 | 700 |  |  |  | 26 |  | 400 | 26 | 52
38 | HPSV STREET LIGHT | 418.7 | kamta sariya-2 | EDD-I SITAPUR | 5391722308 | SS21686437 | 30 kW | 418.75 | 419.35 | 600 |  |  |  | 28 |  | 400 | 28 | 56
Total No Light Fixture for Replacement | [10 empty] | 0 | 0 | 342 | 560 | 338 |  | 1240 | 2480
Non-working/Damaged Light Fixture | [17 empty] | 70
Total | [17 empty] | 2550

## Damaged LED Light Replacement
Damaged/Non working LED light Fixture
SR NO | Equipment Name | Chainage | Village Name | Description | Chainage |  | Total No of Light Fixture | Nonworking/Damaged Light fixture Light |  |  | Remark
[5 empty] | From | To |  | LHS | RHS
1 | LED STREET LIGHT | 290.6 | Shalpur Navdia ROB | Flyover/ROB | 290.05 | 291.35 | 166 | 7 | 10 | 17
2 | LED STREET LIGHT | 403.4 | Hempur ROB RHS | ROB | 402.6 | 404 | 236 | 10 | 17 | 27 | Due damaged crass barrier in , 5 No.s Pole are collaps & 3 Pole are are collaps in service road .
3 | LED STREET LIGHT | 413.83 | Naveen Chowk, VUP | VOP | 413.83 | 413.83 | 75 | 3 | 8 | 11
4 | LED STREET LIGHT | 416.65 | Bahuguda Chauraha Bridge | Flyover/VUP | 416.34 | 417.06 | 116 | 9 | 6 | 15
Total | [7 empty] | 29 | 41 | 70

## Under Pass Lighting
Location for underpass lighting
SR NO | Chainage | Village Name | Description | No of Wallmounted light Fixture for installation | Remark
1 | 270.105 | Faridpur Bypass | VUP | 6 | Wallmounted Light not installed
2 | 274.18 | NEAR GURUDWARA FARIDPUR | PUP | 4 | Wallmounted Light not installed
3 | 277.78 | Faridpur Bareilly | VUP | 6 | Wallmounted Light not installed
4 | 282.38 | NEELAM VENEER, Stiswa | VUP | 6 | Wallmounted Light not installed
5 | 288.235 | Uchesiya Mod Fatehganj Purbi Near Gupta Restourent | VUP | 6 | Wallmounted Light not installed
6 | 290.41 | Shalpur Navdia ROB | PUP | 4 | Wallmounted Light not installed
7 | 291.02 | Shalpur Navdia | PUP | 4 | Wallmounted Light not installed
8 | 295.4 | Katara | VUP | 6 | Wallmounted Light not installed
9 | 303.685 | Mansoorpur Tilhar Cut | VUP | 6 | Wallmounted Light not installed
10 | 305.445 | Tilahar BHS | VUP | 6 | Wallmounted Light not installed
11 | 314.66 | Street Light | VUP/ROB | 6 | Wallmounted Light not installed
12 | 315.77 | Banthara | VUP | 6 | Wallmounted Light not installed
13 | 325.58 | Bareilly Mod | VUP | 6 | Wallmounted Light not installed
14 | 329.56 | Hardoi Mod | VUP | 6 | Wallmounted Light not installed
15 | 331.97 | NEAR DOON SCHOOL BHS, Ahmadpur Niwazpur | VUP | 6 | Wallmounted Light not installed
16 | 332.26 | New Sattelite Bustand shahjahapur | VUP | 6 | Wallmounted Light not installed
17 | 334.25 | Hathoda, ROB | VUP | 6 | Wallmounted Light not installed
18 | 334.62 | Hathoda, ROB | VUP | 6 | Wallmounted Light not installed
19 | 336.635 | Jamuka, Atsalia | VUP | 6 | Wallmounted Light not installed
20 | 358.095 | Jangbahadurganj | VUP | 6 | Wallmounted Light not installed
21 | 361.615 | Barkheriya Jat | VUP | 6 | Wallmounted Light not installed
22 | 363.69 | Hariyali mod | VUP | 6 | Wallmounted Light not installed
23 | 365.435 | Pihani Mod | VUP | 6 | Wallmounted Light not installed
24 | 370.1 | Chapartala | PUP | 4 | Wallmounted Light not installed
25 | 377.36 | Aurangabad / Maigalganj Bypass | VUP | 6 | Wallmounted Light not installed
26 | 383.65 | Neri, Maholi | VUP | 6 | Wallmounted Light not installed
27 | 388.13 | Bhudiya PO Kachuri, Sitapur | PUP | 4 | Wallmounted Light not installed
28 | 392.455 | Badagaon Maholi | VUP | 6 | Wallmounted Light not installed
29 | 396.15 | Maholi BHS | VUP | 6 | Wallmounted Light not installed
30 | 401.5 |  | PUP | 5 | Wallmounted Light not installed
31 | 402.485 | Hempur ROB RHS | VUP | 6 | Wallmounted Light not installed
32 | 402.95 | Hempur | PUP | 4 | Wallmounted Light not installed
33 | 403.62 | Hempur | PUP | 4 | Wallmounted Light not installed
34 | 407.6 | Katili Bridge BHS | PUP | 5 | Wallmounted Light not installed
35 | 413.84 | Naveen Chowk | VOP | 6 | Wallmounted Light not installed
36 | 416.7 | Bahuguda Chauraha Bridge | VUP | 6 | Wallmounted Light not installed
37 | 417.8 | kamta sariya-1 | VUP | 6 | Wallmounted Light not installed
38 | 418.7 | kamta sariya-2 | PUP | 4 | Wallmounted Light not installed
Total |  |  |  | 210

## Highmast Panel
Location for installation of Highmast Control Panel
SR NO | Equipment Name | Chainage | Highmast Panel | Remark
1 | Highmast | 266.62 | 1 | Panel Rusted & Damaged
2 | Highmast | 266.98 | 1 | Panel Rusted & Damaged
3 | Highmast | 267.16 | 1 | Panel Rusted & Damaged
4 | Highmast | 268.15 | 1 | Panel Rusted & Damaged
5 | Highmast | 270 | 2 | Panel Rusted & Damaged
6 | Highmast | 307 | 1 | Panel Rusted & Damaged
7 | Highmast | 315.75 | 2 | Panel Rusted & Damaged
8 | Highmast | 325.58 | 2 | Panel Rusted & Damaged
9 | Highmast | 329.56 | 2 | Panel Rusted & Damaged
10 | Highmast | 331.7 | 1 | Panel Rusted & Damaged
11 | Highmast | 331.95 | 3 | Panel Rusted & Damaged
12 | Highmast | 334.25 | 1 | Panel Rusted & Damaged
13 | Highmast | 356.35 | 1 | Panel Rusted & Damaged
14 | Highmast | 358.05 | 1 | Panel Rusted & Damaged
15 | Highmast | 360.57 | 1 | Panel Rusted & Damaged
16 | Highmast | 363.65 | 1 | Panel Rusted & Damaged
17 | Highmast | 365.45 | 1 | Panel Rusted & Damaged
18 | Highmast | 372.1 | 2 | Panel Rusted & Damaged
19 | Highmast | 372.35 | 3 | Panel Rusted & Damaged
20 | Highmast | 374.08 | 1 | Panel Rusted & Damaged
21 | Highmast | 383.65 | 1 | Panel Rusted & Damaged
22 | Highmast | 388.13 | 1 | Panel Rusted & Damaged
23 | Highmast | 395.55 | 1 | Panel Rusted & Damaged
24 | Highmast | 401.45 | 1 | Panel Rusted & Damaged
25 | Highmast | 407.6 | 1 | Panel Rusted & Damaged
26 | Highmast | 413.9 | 1 | Panel Rusted & Damaged
Total |  |  | 35

## Highmast Light 400 W
ANNEXURE - B
Project Name:- Bareilly Sitapur Highway project
HIGHMAST LOCATION AS PER SITE CONDITION & LUX CALUCLATION_MIN. 40 LUX
Type of Luminaries
S. No. | Chainage | Side | Location | Highmast | Type of Bulb | Distance From Median In Mtr | LF48-502-025-57-XX 400W LED Floodlight - Total 46000 Lumens | LF48-502-060-57-XX 400W LED Floodlight - Total 50000 Lumens | Remarks - Type of Lux Design
1 | 270+100 | LHS | Shoulder | 1 | HPSV | 35 | 5 | 2 | TYPE -3
2 | 270+100 | RHS | Shoulder | 1 | HPSV | 24 | 5 | 2 | TYPE -3
3 | 274+170 | LHS | Shoulder | 1 | HPSV | 44.3 | 14 | 2 | TYPE -1
4 | 277+770 | LHS | Shoulder | 1 | HPSV | 26 | 5 | 2 | TYPE -3
5 | 277+770 | RHS | Shoulder | 1 | HPSV | 34 | 5 | 2 | TYPE -3
6 | 282+380 | LHS | Shoulder | 1 | HPSV | 28 | 5 | 2 | TYPE -3
7 | 282+380 | RHS | Shoulder | 1 | HPSV | 34.5 | 5 | 2 | TYPE -3
8 | 288+200 | LHS | Shoulder | 1 | HPSV | 28.5 | 5 | 2 | TYPE -3
9 | 288+200 | RHS | Shoulder | 1 | HPSV | 36.5 | 5 | 2 | TYPE -3
10 | 295+400 | LHS | Shoulder | 1 | HPSV | 24 | 5 | 2 | TYPE -3
11 | 295+400 | RHS | Shoulder | 1 | HPSV | 32.6 | 5 | 2 | TYPE -3
12 | 303+620 | RHS | Shoulder | 1 | HPSV | 29.4 | 6 | 2 | TYPE -4
13 | 305+410 | LHS | Shoulder | 1 | HPSV | 24.7 | 5 | 2 | TYPE -3
14 | 305+410 | RHS | Shoulder | 1 | HPSV | 29.6 | 5 | 2 | TYPE -3
15 | 307+000 | RHS | Shoulder | 1 | HPSV | 14 | 6 | 2 | TYPE -4
16 | 315+750 | LHS | Shoulder | 1 | HPSV | 31.6 | 5 | 2 | TYPE -3
17 | 315+750 | RHS | Shoulder | 1 | HPSV | 25.3 | 5 | 2 | TYPE -3
18 | 317+450 | LHS | Shoulder | 1 | HPSV | 23.1 | 6 | 2 | TYPE -4
19 | 325+630 | LHS | Shoulder | 1 | HPSV | 21.5 | 5 | 2 | TYPE -3
20 | 325+630 | RHS | Shoulder | 1 | HPSV | 21.5 | 5 | 2 | TYPE -3
21 | 329+560 | LHS | Shoulder | 1 | HPSV | 29 | 5 | 2 | TYPE -3
22 | 329+560 | RHS | Shoulder | 1 | HPSV | 25 | 5 | 2 | TYPE -3
23 | 331+710 | RHS | Shoulder | 1 | HPSV | 24.4 | 6 | 2 | TYPE -4
24 | 331+900 | LHS | Shoulder | 1 | HPSV | 28.4 | 5 | 2 | TYPE -3
25 | 331+950 | RHS | Shoulder | 1 | HPSV | 34.9 | 5 | 2 | TYPE -3
26 | 332+250 | LHS | Shoulder | 1 | HPSV | 27 | 5 | 2 | TYPE -3
27 | 332+250 | RHS | Shoulder | 1 | HPSV | 27 | 5 | 2 | TYPE -3
28 | 334+210 | LHS | Shoulder | 1 | HPSV | 42.3 | 14 | 2 | TYPE -1
29 | 334+910 | LHS | Shoulder | 1 | HPSV | 30 | 6 | 2 | TYPE -4
30 | 336+590 | RHS | Shoulder | 1 | HPSV | 25.8 | 6 | 2 | TYPE -4
31 | 356+380 | RHS | Shoulder | 1 | HPSV | 16.6 | 6 | 2 | TYPE -4
32 | 358+100 | LHS | Shoulder | 1 | HPSV | 29.7 | 5 | 2 | TYPE -3
33 | 358+100 | RHS | Shoulder | 1 | HPSV | 28.8 | 5 | 2 | TYPE -3
34 | 360+580 | RHS | Shoulder | 1 | HPSV | 30.6 | 6 | 2 | TYPE -4
35 | 361+600 | LHS | Shoulder | 1 | HPSV | 35.3 | 5 | 2 | TYPE -3
36 | 361+600 | RHS | Shoulder | 1 | HPSV | 30 | 5 | 2 | TYPE -3
37 | 363+650 | LHS | Shoulder | 1 | HPSV | 25.4 | 5 | 2 | TYPE -3
38 | 363+670 | RHS | Shoulder | 1 | HPSV | 31.8 | 5 | 2 | TYPE -3
39 | 365+440 | LHS | Shoulder | 1 | HPSV | 29 | 5 | 2 | TYPE -3
40 | 365+440 | RHS | Shoulder | 1 | HPSV | 25.6 | 5 | 2 | TYPE -3
41 | 370+100 | RHS | Shoulder | 1 | HPSV | 29.4 | 5 | 2 | TYPE -3
42 | 370+100 | LHS | Shoulder | 1 | HPSV | 25.6 | 5 | 2 | TYPE -3
43 | 374+080 | RHS | Shoulder | 1 | HPSV | 14.2 | 6 | 2 | TYPE -4
44 | 377+350 | LHS | Shoulder | 1 | HPSV | 37.6 | 5 | 2 | TYPE -3
45 | 377+350 | RHS | Shoulder | 1 | HPSV | 60.6 | 17 | 2 | TYPE -2
46 | 380+050 | RHS | Shoulder | 1 | HPSV | 16.6 | 6 | 2 | TYPE -4
47 | 383+650 | LHS | Shoulder | 1 | HPSV | 46.7 | 14 | 2 | TYPE -1
48 | 383+650 | RHS | Shoulder | 1 | HPSV | 32.2 | 5 | 2 | TYPE -3
49 | 388+130 | LHS | Shoulder | 1 | HPSV | 30 | 5 | 2 | TYPE -3
50 | 388+130 | RHS | Shoulder | 1 | HPSV | 28.7 | 5 | 2 | TYPE -3
51 | 392+470 | LHS | Shoulder | 1 | HPSV | 23.5 | 5 | 2 | TYPE -3
52 | 392+470 | RHS | Shoulder | 1 | HPSV | 33 | 5 | 2 | TYPE -3
53 | 395+550 | RHS | Shoulder | 1 | HPSV | 18.5 | 6 | 2 | TYPE -4
54 | 396+170 | RHS | Shoulder | 1 | HPSV | 27.6 | 6 | 2 | TYPE -4
55 | 401+500 | LHS | Shoulder | 1 | HPSV | 13.6 | 5 | 2 | TYPE -3
56 | 401+500 | RHS | Shoulder | 1 | HPSV | 28.7 | 5 | 2 | TYPE -3
57 | 403+570 | RHS | Shoulder | 1 | HPSV | 24 | 6 | 2 | TYPE -4
58 | 407+600 | LHS | Shoulder | 1 | HPSV | 29.8 | 5 | 2 | TYPE -3
59 | 407+600 | RHS | Shoulder | 1 | HPSV | 27.4 | 5 | 2 | TYPE -3
60 | 412+450 | LHS | Shoulder | 1 | HPSV | 17.4 | 6 | 2 | TYPE -4
61 | 413+900 | LHS | Shoulder | 1 | HPSV | 11.6 | 6 | 2 | TYPE -4
62 | 417+800 | LHS | Shoulder | 1 | HPSV | 31.3 | 5 | 2 | TYPE -3
63 | 417+800 | RHS | Shoulder | 1 | HPSV | 32.2 | 5 | 2 | TYPE -3
64 | 418+690 | LHS | Shoulder | 1 | HPSV | 13.6 | 6 | 2 | TYPE -4
| Total Nos. of High Mast to replace Luminaries |  |  | 64 |  |  | 375 | 128